{"text_format":"2","workbook":"xlsx","n_sheets":5,"sheets":["종합","765송부","345송부","154송부","시송전설비"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":16,"comments":2,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"종합","index":0,"n_rows":37,"n_cols":33,"rows_kept":37,"cut":false,"hidden":true,"merged":[[0,0,0,15],[7,14,7,15],[7,1,7,2],[8,1,8,2],[7,9,7,13],[7,3,7,6],[8,3,8,6],[14,14,14,15],[10,1,10,2],[11,1,11,2],[14,9,14,13],[9,1,9,2],[14,2,14,6],[11,3,11,6],[10,3,10,6],[9,3,9,6]]}
[{"$f":"\"'20년 \"&R15&\"월 휴전심의 결과\"","v":"'20년 4월 휴전심의 결과"}]
[]
[]
[]
[]
[]
["◎ 전체 심의결과"]
["전   압","신 청",null,"채 택",null,null,null,"일정\n조정","불채택","(병행/취소/연기)",{"$nulls":4},"연간계획반영(%)"]
["765kV",{"$f":"MAX(#REF!)","v":{"$error":"#REF!"}},null,{"$f":"B9-I9","v":{"$error":"#REF!"}},null,null,null,{"$f":"COUNTIF(#REF!,\"일정조정\")","v":{"$error":"#REF!"}},{"$f":"SUM(J9,L9,N9)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"병행\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"취소\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"연기\")","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"Y\")","v":{"$error":"#REF!"}},{"$f":"(O9/B9)","v":{"$error":"#REF!"}}]
["345kV",{"$f":"MAX(#REF!)","v":{"$error":"#REF!"}},null,{"$f":"B10-I10","v":{"$error":"#REF!"}},null,null,null,{"$f":"COUNTIF(#REF!,\"일정조정\")","v":{"$error":"#REF!"}},{"$f":"SUM(J10,L10,N10)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"병행\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"취소\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"연기\")","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"Y\")","v":{"$error":"#REF!"}},{"$f":"(O10/B10)","v":{"$error":"#REF!"}}]
["154kV",{"$f":"MAX(#REF!)","v":{"$error":"#REF!"}},null,{"$f":"B11-I11","v":{"$error":"#REF!"}},null,null,null,{"$f":"COUNTIF(#REF!,\"일정조정\")","v":{"$error":"#REF!"}},{"$f":"SUM(J11,L11,N11)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"병행\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"취소\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"연기\")","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"Y\")","v":{"$error":"#REF!"}},{"$f":"(O11/B11)","v":{"$error":"#REF!"}}]
["계",{"$f":"SUM(B9:B11)","v":{"$error":"#REF!"}},null,{"$f":"SUM(D9:D11)","v":{"$error":"#REF!"}},null,null,null,{"$f":"SUM(H9:H11)","v":{"$error":"#REF!"}},{"$f":"SUM(J12,L12,N12)","v":{"$error":"#REF!"}},{"$f":"SUM(J9:J11)","v":{"$error":"#REF!"}},"/",{"$f":"SUM(L9:L11)","v":{"$error":"#REF!"}},"/",{"$f":"SUM(N9:N11)","v":{"$error":"#REF!"}},{"$f":"SUM(O9:O11)","v":{"$error":"#REF!"}},{"$f":"(O12/B12)","v":{"$error":"#REF!"}}]
[]
["◎ 본부별 심의결과",{"$nulls":16},"월"]
["사업소","신 청","(765/345/154)",{"$nulls":4},"채 택","불채택","(병행/취소/연기)",{"$nulls":4},"연간계획반영(%)",null,null,4]
["서   울",{"$f":"SUM(C16:G16)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"서울\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"서울\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"서울\")","v":{"$error":"#REF!"}},{"$f":"B16-I16","v":{"$error":"#REF!"}},{"$f":"SUM(J16,L16,N16)","v":{"$error":"#REF!"}},{"$f":"SUM(S16:U16)","v":{"$error":"#REF!"}},"/",{"$f":"SUM(W16:Y16)","v":{"$error":"#REF!"}},"/",{"$f":"SUM(AA16:AC16)","v":{"$error":"#REF!"}},{"$f":"SUM(AE16:AG16)","v":{"$error":"#REF!"}},{"$f":"(O16/B16)","v":{"$error":"#REF!"}},null,"서울",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R16)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R16)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R16)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R16)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R16)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R16)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R16)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R16)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R16)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R16)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R16)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R16)","v":{"$error":"#REF!"}}]
["남서울",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"남서울\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"남서울\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"남서울\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$f":"SUM(J17,L17,N17)","v":{"$error":"#REF!"}},{"$f":"SUM(S17:U17)","v":{"$error":"#REF!"}},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"남서울",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R17)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R17)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R17)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R17)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R17)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R17)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R17)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R17)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R17)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R17)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R17)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R17)","v":{"$error":"#REF!"}}]
["인   천",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"인천\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"인천\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"인천\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"인천",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R18)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R18)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R18)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R18)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R18)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R18)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R18)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R18)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R18)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R18)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R18)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R18)","v":{"$error":"#REF!"}}]
["경기북부",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"경기북부\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"경기북부\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"경기북부\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"경기북부",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R19)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R19)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R19)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R19)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R19)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R19)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R19)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R19)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R19)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R19)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R19)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R19)","v":{"$error":"#REF!"}}]
["경   기",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"경기\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"경기\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"경기\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"경기",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R20)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R20)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R20)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R20)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R20)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R20)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R20)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R20)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R20)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R20)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R20)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R20)","v":{"$error":"#REF!"}}]
["강   원",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"강원\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"강원\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"강원\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"강원",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R21)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R21)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R21)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R21)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R21)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R21)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R21)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R21)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R21)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R21)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R21)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R21)","v":{"$error":"#REF!"}}]
["충   북",{"$f":"SUM(C22:G22)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"충북\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"충북\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"충북\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"충북",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R22)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R22)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R22)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R22)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R22)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R22)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R22)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R22)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R22)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R22)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R22)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R22)","v":{"$error":"#REF!"}}]
["대전충남",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"대전충남\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"대전충남\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"대전충남\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"대전충남",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R23)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R23)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R23)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R23)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R23)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R23)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R23)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R23)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R23)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R23)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R23)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R23)","v":{"$error":"#REF!"}}]
["전   북",{"$f":"SUM(C24:G24)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"전북\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"전북\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"전북\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"전북",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R24)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R24)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R24)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R24)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R24)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R24)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R24)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R24)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R24)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R24)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R24)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R24)","v":{"$error":"#REF!"}}]
["광주전남",{"$f":"SUM(C25:G25)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"광주전남\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"광주전남\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"광주전남\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"광주전남",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R25)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R25)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R25)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R25)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R25)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R25)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R25)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R25)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R25)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R25)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R25)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R25)","v":{"$error":"#REF!"}}]
["대구",{"$f":"SUM(C26:G26)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"대구\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"대구\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"대구\")","v":{"$error":"#REF!"}},{"$f":"B26-I26","v":{"$error":"#REF!"}},{"$f":"SUM(J26,L26,N26)","v":{"$error":"#REF!"}},{"$f":"SUM(S26:U26)","v":{"$error":"#REF!"}},"/",{"$f":"SUM(W26:Y26)","v":{"$error":"#REF!"}},"/",{"$f":"SUM(AA26:AC26)","v":{"$error":"#REF!"}},{"$f":"SUM(AE26:AG26)","v":{"$error":"#REF!"}},{"$f":"(O26/B26)","v":{"$error":"#REF!"}},null,"대구",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R26)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R26)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R26)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R26)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R26)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R26)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R26)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R26)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R26)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R26)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R26)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R26)","v":{"$error":"#REF!"}}]
["경북",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"경북\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"경북\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"경북\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"경북",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R27)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R27)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R27)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R27)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R27)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R27)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R27)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R27)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R27)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R27)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R27)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R27)","v":{"$error":"#REF!"}}]
["부산울산",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"부산울산\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"부산울산\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"부산울산\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},null,"부산울산",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R28)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R28)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R28)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R28)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R28)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R28)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R28)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R28)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R28)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R28)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R28)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R28)","v":{"$error":"#REF!"}}]
["경   남",{"$error":"#REF!"},{"$f":"COUNTIF(#REF!,\"경남\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"경남\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"경남\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$f":"SUM(W29:Y29)","v":{"$error":"#REF!"}},"/",{"$f":"SUM(AA29:AC29)","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},null,"경남",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R29)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R29)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R29)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R29)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R29)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R29)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R29)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R29)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R29)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R29)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R29)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R29)","v":{"$error":"#REF!"}}]
["제   주",{"$f":"SUM(C30:G30)","v":{"$error":"#REF!"}},{"$f":"COUNTIF(#REF!,\"제주\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"제주\")","v":{"$error":"#REF!"}},"/",{"$f":"COUNTIF(#REF!,\"제주\")","v":{"$error":"#REF!"}},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},"/",{"$error":"#REF!"},"/",{"$error":"#REF!"},{"$error":"#REF!"},{"$f":"(O30/B30)","v":{"$error":"#REF!"}},null,"제주",{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R30)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R30)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"병행\",#REF!,R30)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R30)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R30)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"취소\",#REF!,R30)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R30)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R30)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"연기\",#REF!,R30)","v":{"$error":"#REF!"}},null,{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R30)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R30)","v":{"$error":"#REF!"}},{"$f":"COUNTIFS(#REF!,\"y\",#REF!,R30)","v":{"$error":"#REF!"}}]
[]
[" 붙임 :  1. 집중심의내역 1부"]
[" 붙임 :  전압별 검토서 1부. 끝."]
[]
[null,{"$f":"SUM(B16:B30)","v":{"$error":"#REF!"}},{"$f":"SUM(C16:C30)","v":{"$error":"#REF!"}},null,{"$f":"SUM(E16:E30)","v":{"$error":"#REF!"}},null,{"$f":"SUM(G16:G30)","v":{"$error":"#REF!"}},{"$f":"SUM(H16:H30)","v":{"$error":"#REF!"}},{"$f":"SUM(I16:I30)","v":{"$error":"#REF!"}},{"$f":"SUM(J16:J30)","v":{"$error":"#REF!"}},null,{"$f":"SUM(L16:L30)","v":{"$error":"#REF!"}},null,{"$f":"SUM(N16:N30)","v":{"$error":"#REF!"}},{"$f":"SUM(O16:O30)","v":{"$error":"#REF!"}}]
[{"$f":"COUNTIF(B36:N36,\"NO\")","v":0},{"$f":"IF(B35=B12,\"\",\"NO\")","v":{"$error":"#REF!"}},{"$f":"IF(C35=B9,\"\",\"NO\")","v":{"$error":"#REF!"}},null,{"$f":"IF(E35=B10,\"\",\"NO\")","v":{"$error":"#REF!"}},null,{"$f":"IF(G35=B11,\"\",\"NO\")","v":{"$error":"#REF!"}},{"$f":"IF(H35=D12,\"\",\"NO\")","v":{"$error":"#REF!"}},{"$f":"IF(I35=I12,\"\",\"NO\")","v":{"$error":"#REF!"}},{"$f":"IF(J35=J12,\"\",\"NO\")","v":{"$error":"#REF!"}},null,{"$f":"IF(L35=L12,\"\",\"NO\")","v":{"$error":"#REF!"}},null,{"$f":"IF(N35=N12,\"\",\"NO\")","v":{"$error":"#REF!"}}]
[{"$f":"IF(A36>=1,\"틀린곳\",\"\")","v":""},{"$f":"IF(B36=\"NO\",\"총계\",\"\")","v":{"$error":"#REF!"}},{"$f":"IF(C36=\"NO\",\"765\",\"\")","v":{"$error":"#REF!"}},{"$f":"IF(D36=\"NO\",\"총계\",\"\")","v":""},{"$f":"IF(E36=\"NO\",\"345\",\"\")","v":{"$error":"#REF!"}},"",{"$f":"IF(G36=\"NO\",\"154\",\"\")","v":{"$error":"#REF!"}},{"$f":"IF(H36=\"NO\",\"채택\",\"\")","v":{"$error":"#REF!"}},{"$f":"IF(I36=\"NO\",\"불채택\",\"\")","v":{"$error":"#REF!"}},{"$f":"IF(J36=\"NO\",\"병행\",\"\")","v":{"$error":"#REF!"}},"",{"$f":"IF(L36=\"NO\",\"취소\",\"\")","v":{"$error":"#REF!"}},"",{"$f":"IF(N36=\"NO\",\"연기\",\"\")","v":{"$error":"#REF!"}}]

{"sheet":"765송부","index":1,"n_rows":30,"n_cols":13,"rows_kept":30,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,12,3,12],[2,2,3,2],[2,11,3,11]]}
["2020년도 4월 휴전계획서"]
["765kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분","연간반영\n(Y/N)","처리결과\n(Y/N)"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"경기북부","구리","신가평S/S #4 M.Tr","20년도 신가평S/S 765kV #4M.Tr 정밀점검 공사","20년도 신가평S/S 765kV #4M.Tr, #4M.Tr 1차 GIS 정밀점검 공사","2020-04-13 10:00","2020-06-23 18:00","2020-04-13 10:00","2020-06-23 18:00","연속"]
[2,"경기","성남","신안성S/S #2 M.Tr A-1","20년 성남전력 765kV 주변압기 보통점검공사","신안성S/S 765kV #2 M.Tr 보통점검","2020-04-16 09:00","2020-04-26 18:00","2020-04-16 09:00","2020-04-26 18:00","연속"]
[3,"강원","태백","신태백S/S #4 M.Tr","신태백S/S 345kV 용량부족 차단기 대체공사","1. 345kV 77BAY 대체(가덕산풍력 1CB증설 포함) 2. 765kV 8572 CB 유압장치 교체","2020-04-09 09:00","2020-07-15 18:00","2020-04-09 09:00","2020-07-15 18:00","연속"]
[4,"충북","직할","765kV 신서산-신중부#2T/L CB A","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검","2020-04-06 09:00","2020-04-07 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[5,"충북","직할","신서산-신중부#1T/L-#4 M.Tr 1차 TIE CB A","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검","2020-04-22 09:00","2020-04-23 18:00","취소","취소","연속"]
[6,"충북","직할","765kV 신중부-신안성 #1T/L CB A","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검","2020-04-13 09:00","2020-04-14 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[7,"충북","직할","신중부신안성#1 T/L","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검, YPP보호반성능개선","2020-04-13 09:00","2020-04-17 18:00","취소","취소","연속"]
[8,"충북","직할","765kV 신중부-신안성 #1T/L-TIE CB A","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검","2020-04-16 09:00","2020-04-17 18:00","2020-04-16 09:00","2020-04-17 18:00","연속"]
[9,"충북","직할","765kV 신중부-신안성 #2T/L CB A","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검","2020-04-27 09:00","2020-04-28 18:00","2020-04-27 09:00","2020-04-28 18:00","연속"]
[10,"충북","직할","신서산신중부#2 T/L","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검, YPP보호반성능개선","2020-04-06 09:00","2020-04-09 18:00","2020-04-07 09:00","2020-04-07 18:00","연속"]
[11,"충북","직할","765kV 신서산-신중부#2T/L-TIE CB A","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검","2020-04-08 09:00","2020-04-09 18:00","2020-04-16 09:00","2020-04-17 18:00","연속"]
[12,"충북","직할","765kV 신서산-신중부#1T/L CB A","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검","2020-04-20 09:00","2020-04-21 18:00","취소","취소","연속"]
[13,"충북","직할","신중부신안성#2 T/L","765kV 신중부S/S 초기점검공사","800kV GIS 초기점검, YPP보호반성능개선","2020-04-27 09:00","2020-04-30 18:00","취소","취소","연속"]
[14,"대전충남","서산","신서산신중부#1 T/L","[송전]765kV 신서산-신중부#1T/L 정밀점검","[송전]765kV 신서산-신중부#1T/L 신서산ST ~ 신중부ST(173기)","2020-04-20 08:00","2020-04-29 18:00","2020-04-08 08:00","2020-04-12 18:00","연속"]
[15,"대전충남","서산","신서산당진TP#2 T/L","765kV 신서산-당진화력#2T/L 정밀점검","No.1 등 90기","2020-04-27 07:00","2020-05-02 18:00","취소","취소","연속"]
[16,"대전충남","서산","신서산S/S #3 M.Tr","20년 서산P/O 765kV M.Tr 정밀점검공사","신서산S/S 765kV #3M.Tr 정밀점검","2020-04-27 09:00","2020-06-26 18:00","취소","취소","연속"]
[17,"대전충남","서산","신서산당진TP#1 T/L","765kV 신서산-당진화력#1T/L 정밀점검","No.1 등 90기","2020-04-20 07:00","2020-04-25 18:00","취소","취소","연속"]
[18,"경북","영주","신한울S/S #2 M.Tr A-1","YPP계전기 성능개선","- YPP계전기 성능개선","2020-04-07 09:00","2020-04-08 18:00","취소","취소","연속"]
[19,"부산울산","동부산","신고리N/P #2 Tie-Tr","고리NP S/Y 현대제 362kV GIS 구조개선공사 시험가압","고리NP S/Y 현대제 362kV GIS 구조개선공사 시험가압(신고리-고리#2T/L)","2020-04-10 18:00","2020-04-11 18:00","2020-04-10 18:00","2020-04-11 18:00","연속"]
[20,"부산울산","동부산","신고리N/P #2 Tie-Tr","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(신고리S/S #2M.Tr)","2020-04-03 18:00","2020-04-04 18:00","2020-04-03 18:00","2020-04-04 18:00","연속"]
[21,"부산울산","동부산","신고리N/P #1 Tie-Tr","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7872)","2020-04-20 18:00","2020-04-21 18:00","2020-04-20 18:00","2020-04-21 18:00","연속"]
[22,"부산울산","동부산","신고리N/P #1 Tie-Tr","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7800)","2020-04-27 18:00","2020-04-28 18:00","2020-04-27 18:00","2020-04-28 18:00","연속"]
[23,"경남","함안","신고리NP#1T/L-#4M.Tr TIE CB","765kV 북경남SS GIS(8600CB) 보통점검","765kV 북경남SS GIS(8600CB) 보통점검","2020-04-27 09:00","2020-04-28 18:00","2020-04-27 09:00","2020-04-28 18:00","연속"]
[24,"경남","함안","북경남S/S 765kV 북경남-신고리NP#1T/L CB","765kV 북경남SS GIS(8671CB) 보통점검","765kV 북경남SS GIS(8671CB) 보통점검","2020-04-24 09:00","2020-04-25 18:00","2020-04-24 09:00","2020-04-25 18:00","연속"]
[25,"경남","함안","신고리NP#2T/L-#3M.Tr TIE CB","765kV 북경남SS GIS(8500CB) 보통점검","765kV 북경남SS GIS(8500CB) 보통점검","2020-04-22 09:00","2020-04-23 18:00","2020-04-22 09:00","2020-04-23 18:00","연속"]
[26,"경남","함안","북경남-신고리NP#2T/L CB","765kV 북경남SS GIS(8571CB) 보통점검","765kV 북경남SS GIS(8571CB) 보통점검","2020-04-20 09:00","2020-04-21 18:00","2020-04-20 09:00","2020-04-21 18:00","연속"]

{"sheet":"345송부","index":2,"n_rows":245,"n_cols":13,"rows_kept":245,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,12,3,12],[2,2,3,2],[2,11,3,11]]}
["2020년도 4월 휴전계획서"]
["345kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분","연간반영\n(Y/N)","처리결과\n(Y/N)"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"서울","성동","성동S/S 345kV #1 Sh.R 1차 CB (7179)","성동S/S 345kV #1Sh.R 차단기 정밀점검","다빈도 개폐에 따른 차단기 정밀점검공사 시행","2020-04-20 09:00","2020-04-24 18:00","취소","취소","연속"]
[2,"남서울","동서울","동서울S/S #4 M.Tr","서울 동남권지역 전기공급시설 전력구공사(동서울#2-강남5차)","전력구 흙막이 해체작업(H-Pile 인발)","2020-04-01 09:00","2020-04-01 18:00","취소","취소","연속"]
[3,"남서울","동서울","동서울S/S #3 M.Tr","서울 동남권지역 전기공급시설 전력구공사(동서울#2-강남5차)","전력구 흙막이 해체작업(H-Pile 인발)","2020-04-06 09:00","2020-04-06 18:00","2020-04-06 09:00","2020-04-07 18:00","연속"]
[4,"남서울","영등포","신광명S/S 345kV 신시흥#2T/L-#1 M.Tr 1차 TIE CB A (7400A)","신광명S/S 345kV GCB 보통점검(7400)","- CB번호 : 7400 - 345kV 7400 BUS TIE GCB 보통점검 - SF6 가스 수분 및 SO2 측정 - 차단기 개폐타임 측정 - 차단기 메커니즘 점검 - 코일저항 및 절연저항 측정","2020-04-21 09:00","2020-04-21 18:00","2020-04-21 09:00","2020-04-21 18:00","연속"]
[5,"남서울","영등포","신광명S/S #2 M.Tr","신광명S/S 345kV #2 M.Tr 보통점검","- M.Tr 보통점검 - GCB, GIS 보통점검 - VCB 보통점검 및 절연유, 부싱절연유 채유 - 유입식 Sh.R 보통점검 - 1,2,3차 LA 보통점검 및 CVT 점검","2020-04-06 09:00","2020-04-08 18:00","2020-04-06 09:00","2020-04-08 18:00","연속"]
[6,"남서울","영등포","신시흥신광명#2 T/L","신광명S/S 345kV GCB 보통점검","- GCB 보통점검 - 전자변 교체","2020-04-09 09:00","2020-04-09 18:00","2020-04-09 09:00","2020-04-09 18:00","연속"]
[7,"남서울","영등포","신광명영등포#1 T/L","신광명S/S 345kV GIS 보통점검(신광명-영등포#1T/L)","- 345kV GIS 보통점검 - SF6 가스 수분 및 SO2 측정 - 차단기 개폐타임 측정 - 절연저항 측정","2020-04-11 09:00","2020-04-11 18:00","취소","취소","연속"]
[8,"남서울","영등포","신광명S/S #1 M.Tr","신광명S/S 345kV #1 M.Tr 보통점검","- M.Tr 보통점검 - 345kV GCB, 170kV GIS 보통점검 - 3차 VCB, Sh.R 점검 - LA 점검 및 절연유 채유 등","2020-04-01 09:00","2020-04-03 18:00","2020-04-16 09:00","2020-04-18 18:00","연속"]
[9,"남서울","영등포","신광명영등포#2 T/L","신광명S/S 345kV GIS 보통점검","- 345kV GIS 보통점검 - SF6 수분 및 SO2 측정 - 차단기 개폐타임 측정 - 코일 저항 측정 - 차단기 메커니즘 점검","2020-04-12 09:00","2020-04-12 18:00","취소","취소","연속"]
[10,"남서울","영등포","신광명S/S #4 M.Tr","신광명S/S 345kV #4 M.Tr GCB 보통점검","- 345kV GCB 보통점검 - 170kV GIS 하자점검 - 3차 VCB 보통점검 - 2차 LA 보통점검 - #4-1 Sh.R 보통점검 및 #4-1,2 Sh.R CB 조작시험 - 절연유 채유 및 부싱 절연열화 측정(B,C상)","2020-04-16 09:00","2020-04-17 18:00","2020-04-01 09:00","2020-04-02 18:00","연속"]
[11,"남서울","영등포","신광명S/S #3 M.Tr","신광명S/S 345kV #3M.Tr GCB 보통점검","- 345kV GCB 보통점검 - 170kV GIS 하자점검 - 3차 VCB 보통점검 - #3-1,2 Sh.R 보통점검 및 CB 보통점검 - 절연유 채유 및 절연열화 측정 등","2020-04-13 09:00","2020-04-14 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[12,"남서울","직할","영등포S/S 345kV #75 BUS","영등포S/S #4M.Tr 증설","362kV GIS x 3CB 345kV M.Tr x 1 Bank 170kV GIS x 1CCT","2020-04-29 18:00","2020-05-06 18:00","2020-05-06 18:00","2020-05-13 18:00","연속"]
[13,"남서울","직할","영등포S/S 345kV #70 BUS","영등포S/S #4M.Tr 증설","362kV GIS x 3CB 345kV M.Tr x 1 Bank 170kV GIS x 1CCT","2020-04-22 09:00","2020-04-29 18:00","2020-04-30 09:00","2020-05-06 18:00","연속"]
[14,"남서울","직할","영등포S/S 345kV #1 Sh.R","영등포S/S 345kV GIS 정밀점검공사","영등포S/S 345kV GIS 정밀점검공사 다빈도 차단기 정밀점검","2020-04-06 09:00","2020-04-10 18:00","취소","취소","연속"]
[15,"남서울","직할","영등포S/S 345kV #2 Sh.R","영등포S/S 345kV GIS 정밀점검공사","영등포S/S 345kV GIS 정밀점검공사 다빈도 차단기 정밀점검","2020-04-13 09:00","2020-04-17 18:00","취소","취소","연속"]
[16,"인천","김포","가정개폐소 345kV #75 BUS","345kV 갈산S/S 건설사업","O 345kV M.Tr 500MVA 3Bank O 362kV GIS 15CCT O 170kV GIS 11CCT 등","2020-04-20 09:00","2020-04-21 18:00","2020-04-20 09:00","2020-04-21 18:00","연속"]
[17,"인천","김포","가정개폐소 345kV #76 BUS","345kV 갈산S/S 건설사업","O 345kV M.Tr 500MVA 3Bank O 362kV GIS 15CCT O 170kV GIS 11CCT 등","2020-04-20 09:00","2020-04-21 18:00","2020-04-20 09:00","2020-04-21 18:00","연속"]
[18,"인천","김포","가정인천CC#1 T/L","345kV 갈산S/S 건설사업","O 345kV M.Tr 500MVA 3Bank O 362kV GIS 15CCT O 170kV GIS 11CCT 등","2020-04-14 09:00","2020-04-14 18:00","2020-04-14 09:00","2020-04-14 18:00","연속"]
[19,"인천","김포","가정개폐소 345kV #76 BUS","345kV 갈산S/S 건설사업","O 345kV M.Tr 500MVA 3Bank O 362kV GIS 15CCT O 170kV GIS 11CCT 등","2020-04-13 09:00","2020-04-14 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[20,"인천","김포","가정개폐소 345kV 가정-갈산#3T/L TIE CB A (7200A)","345kV 갈산S/S 건설사업","o 345kV 500MVA 3Bank o 362kV GIS 15CCT o 170kV GIS 11CCT 등","2020-04-06 09:00","2020-04-10 18:00","2020-04-06 09:00","2020-04-10 18:00","연속"]
[21,"인천","김포","신가좌가정#2 T/L","345kV 갈산S/S 건설사업","O 345kV M.Tr 500MVA 3Bank O 362kV GIS 15CCT O 170kV GIS 11CCT 등","2020-04-09 09:00","2020-04-09 18:00","2020-04-09 09:00","2020-04-09 18:00","연속"]
[22,"인천","김포","가정인천CC#2 T/L","345kV 갈산S/S 건설사업","O 345kV M.Tr 500MVA 3Bank O 362kV GIS 15CCT O 170kV GIS 11CCT 등","2020-04-07 09:00","2020-04-07 18:00","2020-04-07 09:00","2020-04-07 18:00","연속"]
[23,"인천","김포","가정개폐소 345kV 신가좌-가정#2T/L TIE CB A (7300A)","345kV 갈산S/S 건설사업","o 345kV M.Tr 500MVA 3Bank o 362kV GIS 15CCT o 170kV GIS 11CCT","2020-04-06 09:00","2020-04-10 18:00","취소","취소","연속"]
[24,"인천","김포","가정개폐소 345kV #75 BUS","345kV 갈산S/S 건설사업","O 345kV M.Tr 500MVA 3Bank O 362kV GIS 15CCT O 170kV GIS 11CCT 등","2020-04-06 09:00","2020-04-10 18:00","2020-04-06 09:00","2020-04-10 18:00","연속"]
[25,"인천","김포","가정개폐소 345kV 가정-갈산#1T/L TIE CB A (7400A)","345kV 갈산S/S 건설사업","o 345kV M.Tr 500MVA 3Bank o 362kV GIS 15CCT o 170kV GIS 11CCT","2020-04-13 09:00","2020-04-14 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[26,"인천","부평","서인천C/C 345kV #70-72 CLR #7077 CB A (7077_A)","서인천복합S/Y 7077GIS 조작시험","서인천복합S/Y 7077GIS 조작시험","2020-04-08 09:00","2020-04-08 13:00","2020-04-08 09:00","2020-04-08 13:00","연속"]
[27,"인천","부평","서인천C/C 345kV #70-72 CLR #7277 CB A (7277_A)","서인천복합S/Y 7277GIS 조작시험","서인천복합S/Y 7277GIS 조작시험","2020-04-08 13:00","2020-04-08 18:00","2020-04-08 13:00","2020-04-08 18:00","연속"]
[28,"인천","부평","서인천C/C 345kV #75-77 CLR #7577 CB A (7577_A)","서인천복합S/Y 7577GIS 조작시험","서인천복합S/Y 7577GIS 조작시험","2020-04-09 09:00","2020-04-09 13:00","2020-04-09 09:00","2020-04-09 13:00","연속"]
[29,"인천","부평","서인천C/C 345kV #75-77 CLR #7777 CB A (7777_A)","서인천복합S/Y 7777GIS 조작시험","서인천복합S/Y 7777GIS 조작시험","2020-04-09 13:00","2020-04-09 18:00","2020-04-09 13:00","2020-04-09 18:00","연속"]
[30,"인천","부평","서인천C/C 345kV 신경서서인천CCT/L-#2 M.Tr 1차 TIE CB A (7200_A)","서인천복합S/Y 7200GIS 조작시험","서인천복합S/Y 7200GIS 조작시험","2020-04-10 09:00","2020-04-10 13:00","2020-04-10 09:00","2020-04-10 13:00","연속"]
[31,"인천","부평","서인천C/C 345kV 신경서-서인천CC T/L CB A (7271_A)","서인천복합S/Y 7271GIS 조작시험","서인천복합S/Y 7271GIS 조작시험","2020-04-10 13:00","2020-04-10 18:00","2020-04-10 13:00","2020-04-10 18:00","연속"]
[32,"인천","부평","서인천C/C 345kV #2 M.Tr 1차 CB A (7272_A)","서인천복합S/Y 7272GIS 조작시험","서인천복합S/Y 7272GIS 조작시험","2020-04-14 09:00","2020-04-14 13:00","2020-04-14 09:00","2020-04-14 13:00","연속"]
[33,"인천","부평","서인천C/C 345kV #3 M.Tr 1차 CB A (7372_A)","서인천복합S/Y 7372GIS 조작시험","서인천복합S/Y 7372GIS 조작시험","2020-04-14 13:00","2020-04-14 18:00","2020-04-14 13:00","2020-04-14 18:00","연속"]
[34,"인천","부평","서인천C/C 345kV #1 Sh.R","서인천복합S/Y #1Sh.R 휴전작업","-서인천복합S/Y #1Sh.R 하자점검 -서인천복합S/Y 7379 GIS 조작시험","2020-04-16 09:00","2020-04-16 18:00","2020-04-16 09:00","2020-04-16 18:00","연속"]
[35,"인천","부평","서인천C/C 345kV #2 Sh.R","서인천복합S/Y #2Sh.R 휴전작업","-서인천복합S/Y #2Sh.R 하자점검 -서인천복합S/Y 7479 GIS 조작시험","2020-04-17 09:00","2020-04-17 18:00","2020-04-17 09:00","2020-04-17 18:00","연속"]
[36,"인천","부평","서인천C/C 345kV #4 Sh.R 1차 CB B (7A79_B)","서인천복합S/Y 7A79GIS 조작시험","서인천복합S/Y 7A79GIS 조작시험","2020-04-20 09:00","2020-04-20 13:00","2020-04-20 09:00","2020-04-20 13:00","연속"]
[37,"인천","부평","서인천C/C 345kV #3 Sh.R 1차 CB A (7B79_A)","서인천복합S/Y 7B79GIS 조작시험","서인천복합S/Y 7B79GIS 조작시험","2020-04-20 13:00","2020-04-20 18:00","2020-04-20 13:00","2020-04-20 18:00","연속"]
[38,"인천","부평","서인천C/C 345kV #4 M.Tr 1차 CB A (7472_A)","서인천복합S/Y 7472GIS 조작시험","서인천복합S/Y 7472GIS 조작시험","2020-04-27 09:00","2020-04-27 11:00","2020-04-27 09:00","2020-04-27 11:00","연속"]
[39,"인천","부평","서인천C/C 345kV 서인천CC-신부평#1T/L CB A (7A71_A)","서인천복합S/Y 7A71GIS 하자점검","서인천복합S/Y 7A71GIS 하자점검","2020-04-27 11:00","2020-04-27 18:00","2020-04-27 11:00","2020-04-27 18:00","연속"]
[40,"인천","부평","신가좌가정#2 T/L","345kV 갈산S/S 건설사업","O 345kV M.Tr 500MVA 3Bank O 362kV GIS 15CCT O 170kV GIS 11CCT 등","2020-04-20 09:00","2020-04-21 18:00","2020-04-20 09:00","2020-04-21 18:00","연속"]
[41,"인천","부평","신경서S/S 345kV 신경서-인천CC#2T/L CB A (7372_A)","신경서S/S 7372GIS 조작시험","신경서S/S 7372GIS 조작시험","2020-04-01 13:00","2020-04-01 18:00","2020-04-01 13:00","2020-04-01 18:00","연속"]
[42,"인천","부평","신경서S/S 345kV 신경서-서인천CCT/L CB A (7472_A)","신경서S/S 7472GIS 조작시험","신경서S/S 7472GIS 조작시험","2020-04-02 09:00","2020-04-02 13:00","2020-04-02 09:00","2020-04-02 13:00","연속"]
[43,"인천","부평","신경서S/S 345kV 신경서포스코SY#2T/L-#3 M.Tr 1차T/L TIE CB A (7500_A)","신경서S/S 7500GIS 조작시험","신경서S/S 7500GIS 조작시험","2020-04-02 13:00","2020-04-02 18:00","2020-04-02 13:00","2020-04-02 18:00","연속"]
[44,"인천","부평","신경서S/S 345kV #2 M.Tr 1차 CB A (7272_A)","신경서S/S 7272GIS 조작시험","신경서S/S 7272GIS 조작시험","2020-04-03 09:00","2020-04-03 13:00","2020-04-03 09:00","2020-04-03 13:00","연속"]
[45,"인천","부평","신경서S/S 345kV 신경서-신인천CCT/L CB A (7171_A)","신경서S/S 7171GIS 조작시험","신경서S/S 7171GIS 조작시험","2020-04-01 09:00","2020-04-01 13:00","2020-04-01 09:00","2020-04-01 13:00","연속"]
[46,"인천","부평","신경서S/S 345kV 신경서포스코SY#1-신경서인천CC#2T/L TIE CB A (7300_A)","신경서S/S 7300GIS 조작시험","신경서S/S 7300GIS 조작시험","2020-04-03 13:00","2020-04-03 18:00","2020-04-03 13:00","2020-04-03 18:00","연속"]
[47,"인천","부평","신경서S/S 345kV 신경서-포스코SY#1T/L CB A (7371_A)","신경서S/S 7371GIS 조작시험","신경서S/S 7371GIS 조작시험","2020-04-06 09:00","2020-04-06 13:00","2020-04-06 09:00","2020-04-06 13:00","연속"]
[48,"인천","부평","신경서S/S 345kV 신경서-포스코S/Y#2T/L CB A (7571_A)","신경서S/S 7571GIS 조작시험","신경서S/S 7571GIS 조작시험","2020-04-06 13:00","2020-04-06 18:00","2020-04-06 13:00","2020-04-06 18:00","연속"]
[49,"인천","부평","신경서S/S 345kV 신경서-서인천CCT/L TIE CB B (7400_B)","신경서S/S 7400GIS 조작시험","신경서S/S 7400GIS 조작시험","2020-04-07 09:00","2020-04-07 13:00","2020-04-07 09:00","2020-04-07 13:00","연속"]
[50,"인천","부평","신경서S/S 345kV #3 M.Tr 1차 CB A (7572_A)","신경서S/S 7572GIS 조작시험","신경서S/S 7572GIS 조작시험","2020-04-07 13:00","2020-04-07 18:00","2020-04-07 13:00","2020-04-07 18:00","연속"]
[51,"인천","부평","신경서S/S 345kV #1 M.Tr 1차 CB A (7172_A)","신경서S/S 7172GIS 보통점검","신경서S/S 7172GIS 보통점검","2020-04-08 09:00","2020-04-08 18:00","2020-04-08 09:00","2020-04-08 18:00","연속"]
[52,"인천","부평","신인천C/C 345kV 3MT001 CB A (7671_A)","신인천복합S/Y 7671GIS 조작시험","신인천복합S/Y 7671GIS 조작시험","2020-04-22 09:00","2020-04-22 13:00","2020-04-22 09:00","2020-04-22 13:00","연속"]
[53,"인천","시흥","신가좌신시흥#2 T/L","345kV 신가좌-신시흥(신시흥-신광명)T/L 지장송전선로 이설공사","공사구간 : (하단) 345kV 신가좌-신시흥 #2T/L No.58~59 (상단) 345kV 신시흥-신광명 #2T/L No.35~36 선로길이 : 345kV 신시흥-신광명T/L - 0.4777km 345kV 신가좌-신시흥T/L - 0.4777km","2020-04-27 07:00","2020-05-01 18:00","2020-04-27 07:00","2020-05-01 18:00","연속"]
[54,"인천","시흥","신시흥영흥TP#3 T/L","2020-2021년 송전정비회사 총액공사","345kV 서서울2-신시흥#2T/L 스페이서간격조정에 따른 안전이격거리확보","2020-04-25 13:00","2020-04-25 15:00","2020-04-25 13:00","2020-04-25 15:00","연속"]
[55,"인천","시흥","신시흥#1S/S #1 M.Tr","신시흥S/S PL-LD6 옥외분전반대체(#1M.Tr휴전)","신시흥S/S PL-LD6 옥외분전반대체(#1M.Tr휴전)","2020-04-28 10:00","2020-04-28 18:00","취소","취소","연속"]
[56,"인천","시흥","신시흥신광명#2 T/L","345kV 신가좌-신시흥(신시흥-신광명)T/L 지장송전선로 이설공사","공사구간 : (상단) 345kV 신시흥-신광명 #2T/L No.35~36 (하단) 345kV 신가좌-신시흥 #2T/L No.58~59 선로길이 : 345kV 신시흥-신광명T/L - 0.4777km 345kV 신가좌-신시흥T/L - 0.4777km","2020-04-27 07:00","2020-05-01 18:00","2020-04-27 07:00","2020-05-01 18:00","연속"]
[57,"인천","시흥","서서울#2신시흥#1 T/L","신시흥S/S PL-LA3 옥외분전반대체(서서울2신시흥#1T/L휴전)","신시흥S/S PL-LA3 옥외분전반대체(서서울2신시흥#1T/L휴전)","2020-04-08 10:00","2020-04-08 18:00","취소","취소","연속"]
[58,"인천","시흥","신시흥영흥TP#1 T/L","신시흥S/S PL-LA1 옥외분전반대체(신시흥영흥TP#1T/L휴전)","신시흥S/S PL-LA1 옥외분전반대체(신시흥영흥TP#1T/L휴전)","2020-04-01 10:00","2020-04-01 18:00","2020-04-01 10:00","2020-04-01 18:00","연속"]
[59,"인천","시흥","영흥T/P 345kV #1G.Tr 1차 GIS","영흥#1S/Y 345kV 7172 GIS정밀점검","영흥#1S/Y 345kV 7172 GIS정밀점검","2020-04-13 10:00","2020-04-17 18:00","2020-04-27 10:00","2020-04-30 18:00","연속"]
[60,"인천","시흥","신시흥영흥TP#4 T/L","345kV신시흥영흥#4T/L 사선 현수애자진단","345kV신시흥영흥#4T/L 사선 현수애자진단 -15(수)임시휴일,18(토),19(일) 주말제외","2020-04-13 08:00","2020-04-22 18:00","2020-04-13 08:00","2020-04-22 18:00","매일"]
[61,"인천","시흥","영흥T/P 345kV 영흥TP연락#1T/L-#1G.Tr 1차 TIE GIS","영흥#1S/Y 345kV 7100 GIS정밀점검","영흥#1S/Y 345kV 7100 GIS정밀점검","2020-04-06 10:00","2020-04-10 18:00","2020-04-23 10:00","2020-04-26 18:00","연속"]
[62,"인천","시흥","신시흥영흥TP#3 T/L","345kV신시흥영흥#3T/L 사선 현수애자진단","345kV신시흥영흥#3T/L 사선 현수애자진단 -4(토),5(일) 주말제외","2020-04-02 08:00","2020-04-10 18:00","2020-04-02 08:00","2020-04-10 18:00","매일"]
[63,"인천","시흥","영흥1TP영흥2TP#1 T/L","영흥#1S/Y 345kV 7172GIS정밀점검 무부하가압","영흥#1S/Y 345kV 7172GIS정밀점검 무부하가압","2020-04-17 10:00","2020-04-17 18:00","2020-04-30 10:00","2020-04-30 18:00","연속"]
[64,"인천","시흥","영흥T/P 345kV 신시흥-영흥TP#2T/L GIS","영흥#1S/Y 345kV 신시흥영흥#2T/L(7471) ANN보수","영흥#1S/Y 345kV 신시흥영흥#2T/L(7471) ANN보수","2020-04-27 10:00","2020-04-27 18:00","취소","취소","연속"]
[65,"인천","시흥","영흥1TP영흥2TP#1 T/L","영흥#1S/Y 345kV 7100GIS정밀점검 무부하가압","영흥#1S/Y 345kV 7100GIS정밀점검 무부하가압","2020-04-10 10:00","2020-04-10 18:00","2020-04-26 10:00","2020-04-26 18:00","연속"]
[66,"인천","직할","신부평S/S #1 M.Tr","신부평S/S #1M.Tr 2차 170kV GIS 정밀점검","신부평S/S #1M.Tr 2차 170kV GIS 정밀점검","2020-04-20 09:00","2020-04-22 18:00","2020-04-20 09:00","2020-04-22 18:00","연속"]
[67,"인천","직할","서인천CC신부평#2 T/L","345kV 서인천CC-신부평#2T/L 절연유 보충","345kV 서인천CC-신부평#2T/L 절연유 보충","2020-04-17 09:00","2020-04-17 18:00","2020-04-17 09:00","2020-04-17 18:00","연속"]
[68,"인천","직할","서인천CC신부평#3 T/L","345kV 서인천CC-신부평#3T/L 절연유 보충","345kV 서인천CC-신부평#3T/L 절연유 보충","2020-04-23 09:00","2020-04-23 18:00","2020-04-23 09:00","2020-04-23 18:00","연속"]
[69,"인천","직할","서인천CC신부평#4 T/L","345kV 서인천CC-신부평#4T/L 절연유 보충","345kV 서인천CC-신부평#4T/L 절연유 보충","2020-04-24 09:00","2020-04-24 18:00","취소","취소","연속"]
[70,"인천","직할","신부평S/S #3 M.Tr","신부평S/S #3M.Tr 2차 170kV GIS 정밀점검","신부평S/S #3M.Tr 2차 170kV GIS 정밀점검","2020-04-27 09:00","2020-04-29 18:00","2020-04-27 09:00","2020-04-29 18:00","연속"]
[71,"인천","직할","신부평S/S #2 M.Tr","신부평S/S #2M.Tr 2차 170kV GIS 정밀점검","신부평S/S #2M.Tr 2차 170kV GIS 정밀점검","2020-04-30 09:00","2020-05-02 18:00","취소","취소","연속"]
[72,"경기북부","고양","신김포신파주#1 T/L","고양전력지사 OPGW 항공장애표시구 정비공사","345kV 신파주-양주 등 8개T/L OPGW 항공장애표시구 정비공사","2020-04-06 07:00","2020-04-06 18:00","취소","취소","연속"]
[73,"경기북부","고양","신김포신파주#2 T/L","고양전력지사 항공장애표시구 정비공사","345kV 신파주-양주 등 8개T/L 항공장애표시구 정비공사","2020-04-07 07:00","2020-04-07 18:00","취소","취소","연속"]
[74,"경기북부","구리","미금성동#3 T/L","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체 - 미금S/S 교체 75Bay 차단기 3대 감시제어계측 포인트이관 (→SA) - 75Bay LCP 및 배전반 모자익반 제어케이블 철거 및 재결선","2020-04-20 09:00","2020-04-29 18:00","2020-04-20 09:00","2020-04-28 18:00","연속"]
[75,"경기북부","구리","미금S/S STATCOM CB","미금S/S 소음저감대책 적용 공사","방음벽 설치 -#1~#6Sh.R, STATCOM","2020-04-01 09:00","2020-04-03 18:00","2020-04-01 09:00","2020-04-03 18:00","연속"]
[76,"경기북부","구리","동서울미금#2 T/L","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체 - 미금S/S 교체 75Bay 차단기 3대 감시제어계측 포인트이관 (→SA) - 75Bay LCP 및 배전반 모자익반 제어케이블 철거 및 재결선","2020-04-20 09:00","2020-04-29 18:00","2020-04-06 09:00","2020-04-10 18:00","연속"]
[77,"경기북부","구리","동서울미금#1 T/L","미금S/S 감시제어설비 교체공사","장기사용 모자익반 교체 - 미금S/S 교체 74Bay 차단기 2대 감시제어계측 포인트이관 (→SA) - 74Bay LCP 및 배전반 모자익반 제어케이블 철거 및 재결선","2020-04-06 09:00","2020-04-10 18:00","2020-04-06 09:00","2020-04-10 18:00","연속"]
[78,"경기북부","구리","신가평포천LNGCC#2 T/L","345kV 신가평-포천LNGCC#2T/L 송전선로 정밀점검","-신가평S/S~포천LNGCC 철탑 177기 송전선로 정밀점검","2020-04-06 08:30","2020-04-24 18:00","2020-04-06 08:30","2020-04-24 18:00","연속"]
[79,"경기북부","구리","신가평S/S 345kV #75 BUS","345kV GIS 정밀점검공사","345kV GIS 정밀점검공사","2020-04-20 09:00","2020-04-21 18:00","2020-04-20 09:00","2020-04-21 18:00","연속"]
[80,"경기북부","구리","신가평포천LNGCC#1 T/L","345kV GIS LCM 교체공사","345kV GIS LCM 교체공사","2020-04-03 09:00","2020-04-03 18:00","2020-04-03 09:00","2020-04-03 18:00","연속"]
[81,"경기북부","직할","양주S/S #4 M.Tr","20년도 경기북부 직할 변전정비회사 총액공사","양주S/S #4 M.Tr 1차 GIS 보통점검(7172, 7100 GIS)","2020-04-16 09:00","2020-04-17 18:00","2020-04-16 09:00","2020-04-17 18:00","연속"]
[82,"경기북부","직할","양주S/S #2 M.Tr","20년도 경기북부 직할 변전정비회사 총액공사","양주S/S #2 M.Tr 1차 GIS 보통점검(7472 GIS)","2020-04-13 09:00","2020-04-13 18:00","2020-04-13 09:00","2020-04-13 18:00","연속"]
[83,"경기북부","직할","양주중부#1 T/L","20-21년 가공송전 정비회사 총액공사","ㅇ 96년 이전애자 교체","2020-04-07 07:00","2020-04-10 18:00","2020-04-07 07:00","2020-04-10 18:00","연속"]
[84,"경기북부","직할","양주S/S #1 M.Tr","20년도 경기북부 직할 변전정비회사 총액공사","양주S/S #1 M.Tr 1차 GIS 보통점검(7272, 7200GIS)","2020-04-02 09:00","2020-04-03 18:00","2020-04-02 09:00","2020-04-03 18:00","연속"]
[85,"경기북부","직할","양주중부#2 T/L","20-21년 가공송전 정비회사 총액공사","ㅇ 96년 이전애자 교체","2020-04-13 07:00","2020-04-17 18:00","2020-04-13 07:00","2020-04-17 18:00","연속"]
[86,"경기북부","직할","신의정부양주#2 T/L","20년도 경기북부 직할 변전정비회사 총액공사","양주S/S 신의정부-양주 #2 T/L(7271 GIS)","2020-04-21 09:00","2020-04-21 18:00","2020-04-28 13:00","2020-04-29 18:00","연속"]
[87,"경기북부","직할","신의정부양주#1 T/L","20년도 경기북부 직할 변전정비회사 총액공사","양주S/S 신의정부-양주 #1 T/L(7171 GIS)","2020-04-20 09:00","2020-04-20 18:00","2020-04-27 09:00","2020-04-28 13:00","연속"]
[88,"경기","군포","서서울#2신성남#2 T/L","2020-2021년 송전정비회사 총액공사","스페이서 간격 조정 : 360개(본사 지시사항)","2020-04-24 08:00","2020-04-24 18:00","2020-04-24 08:00","2020-04-24 18:00","연속"]
[89,"경기","군포","서서울#2신성남#1 T/L","2020-2021년 송전정비회사 총액공사","스페이서 간격 조정 : 360개(본사 지시사항)","2020-04-23 08:00","2020-04-23 18:00","2020-04-23 08:00","2020-04-23 18:00","연속"]
[90,"경기","군포","서서울#2신시흥#1 T/L","2020-2021년 송전정비회사 총액공사","스페이서 간격 조정 : 2670개(본사 지시사항)","2020-04-20 08:00","2020-04-22 18:00","2020-04-27 08:00","2020-04-29 18:00","연속"]
[91,"경기","군포","서서울S/S #2 M.Tr","서서울#1S/S #2M.Tr 1,2차 GIS 조작/하자점검","345kV 7500,7572 GIS 조작시험 / 2차 GIS 하자점검 / 3차 4299, 4279, 427-1,2 VCB 보통점검","2020-04-20 09:00","2020-04-21 18:00","2020-04-20 09:00","2020-04-21 18:00","연속"]
[92,"경기","군포","서서울S/S #1 M.Tr","서서울#1S/S 345kV #1M.Tr 보통점검","서서울#1S/S 345kV #1M.Tr 보통점검 / 7300,7372 GIS 보통점검 / 1차 LA 보통점검 / 1,2차 붓싱절연유 채유 / 2차 GIS 하자점검 / 4199 VCB 보통점검","2020-04-06 09:00","2020-04-07 18:00","2020-04-06 09:00","2020-04-07 18:00","연속"]
[93,"경기","군포","서서울S/S #4 M.Tr","서서울#1S/S 345kV #4M.Tr 보통점검","서서울#1S/S 345kV #4M.Tr 보통점검 / 7800,7872 GIS 조작시험 / 1,2차 붓싱절연유 채유 / 2차 GIS 하자점검","2020-04-08 09:00","2020-04-09 18:00","2020-04-08 09:00","2020-04-09 18:00","연속"]
[94,"경기","동부","곤지암동서울#2 T/L","20년 동부 변전정비회사 총액공사","곤지암:7400,7471 GIS(보통), 7400(A,B),7471(A,B)전자변교체 43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-04-02 09:30","2020-04-02 18:00","2020-04-02 09:30","2020-04-02 18:00","연속"]
[95,"경기","성남","신성남S/S #3 M.Tr","20년 성남전력지사 변전정비회사 총액공사","1차측 GIS 보통점검(TIE제외), 전자변교체, 부싱절연유채유","2020-04-21 09:00","2020-04-21 18:00","2020-04-21 09:00","2020-04-21 18:00","연속"]
[96,"경기","성남","신수원S/S #2 M.Tr","압력감시장치 설치공사","압력감시장치 설치","2020-04-06 09:00","2020-04-07 18:00","2020-04-06 09:00","2020-04-07 18:00","연속"]
[97,"경기","성남","신수원S/S 345kV 신수원-삼성#1T/L GIS","신수원S/S 345kV 용량부족 GIS 대체공사","- 345kV GIS(40kA, 4000A) × 14CB 철거 - 345kV GIS(63kA, 6300A) × 14CB 신설","2020-04-27 09:00","2020-07-10 18:00","취소","취소","연속"]
[98,"경기","성남","신수원S/S 345kV #70 BUS","신수원S/S 345kV 용량부족 GIS 대체공사","- 345kV GIS(40kA, 4000A) × 14CB 철거 - 345kV GIS(63kA, 6300A) × 14CB 신설","2020-04-27 09:00","2020-05-06 18:00","취소","취소","연속"]
[99,"경기","성남","신수원S/S #3 M.Tr","20년 성남전력지사 변전정비회사 총액공사","C상 초기점검, 1차 GIS 초기점검, 1차 LA 보통점검, 2차 LA 보통점검,부싱절연유채유","2020-04-16 09:00","2020-04-17 18:00","2020-04-16 09:00","2020-04-17 18:00","연속"]
[100,"경기","성남","신수원S/S 345kV 신안성-신수원#2T/L GIS","신수원S/S 345kV 용량부족 GIS 대체공사","- 345kV GIS(40kA, 4000A) × 14CB 철거 - 345kV GIS(63kA, 6300A) × 14CB 신설","2020-04-22 09:00","2020-07-10 18:00","취소","취소","연속"]
[101,"경기","성남","신안성신용인#1 T/L","345kV 신안성-신용인, 신안성-신성남T/L 송전선로 정밀점검","345kV 신안성-신용인T/L 1~66호(66기), 신안성-신성남T/L 1~60호(60기) 송전선로 정밀점검(4회선 구간 2~60호)","2020-04-03 09:00","2020-04-21 18:00","2020-04-03 09:00","2020-04-21 18:00","연속"]
[102,"경기","성남","신안성신성남#1 T/L","345kV 신안성-신용인, 신안성-신성남T/L 송전선로 정밀점검","345kV 신안성-신용인T/L 1~66호(66기), 신안성-신성남T/L 1~60호(60기) 송전선로 정밀점검(4회선 구간 2~60호)","2020-04-03 09:00","2020-04-21 18:00","2020-04-03 09:00","2020-04-21 18:00","연속"]
[103,"경기","성남","신용인S/S #3 M.Tr","20년 성남전력지사 변전정비회사 총액공사","#1DS 전자변 교체","2020-04-02 09:00","2020-04-02 18:00","2020-04-02 09:00","2020-04-02 18:00","연속"]
[104,"경기","성남","신용인S/S #2 M.Tr","20년 성남전력지사 변전정비회사 총액공사","2차 GIS 조작시험, 3차 VCB 조작시험, 1차 LA 초기점검, 3차 LA 초기점검, 부싱절연유채유","2020-04-09 09:00","2020-04-09 18:00","2020-04-09 09:00","2020-04-09 18:00","연속"]
[105,"경기","직할","화성서서울#1 T/L","봉담-송산간 도로개설 관련 지장이설공사(2공구)","18~23호, 가철탑 1기, 전력선 1.799km","2020-04-01 07:00","2020-04-16 18:00","취소","취소","연속"]
[106,"경기","직할","화성서서울#2 T/L","봉담-송산간 도로개설 관련 지장이설공사(2공구)","18~23호, 가철탑 1기, 전력선 1.799km","2020-04-17 07:00","2020-04-24 18:00","취소","취소","연속"]
[107,"경기","직할","화성S/S #3 M.Tr","20년 직할 변전정비회사 총액공사","#3M.Tr 3차측 과열보수 작업","2020-04-08 09:00","2020-04-08 18:00","2020-04-01 09:00","2020-04-01 18:00","연속"]
[108,"경기","평택","고덕S/S 345kV #4 M.Tr CB","고덕S/S 345kV #4 M.Tr 변압기 하자점검","고덕S/S 345kV #4 M.Tr 변압기 하자점검 / #4M.Tr 2차 GIS 하자점검","2020-04-27 10:00","2020-04-29 18:00","2020-04-27 10:00","2020-04-29 18:00","연속"]
[109,"경기","평택","고덕S/S 345kV #1 M.Tr CB","고덕S/S 345kV #1 M.Tr 변압기 하자점검","고덕S/S 345kV #1 M.Tr 변압기 하자점검 / #1M.Tr 2차 GIS 하자점검","2020-04-01 10:00","2020-04-03 18:00","2020-04-01 10:00","2020-04-03 18:00","연속"]
[110,"경기","평택","고덕S/S 345kV #2 M.Tr CB","고덕S/S 345kV #2 M.Tr 변압기 하자점검","고덕S/S 345kV #2 M.Tr 변압기 하자점검 / #2M.Tr 2차 GIS 하자점검","2020-04-06 10:00","2020-04-08 18:00","2020-04-06 10:00","2020-04-08 18:00","연속"]
[111,"경기","평택","고덕S/S 345kV #3 M.Tr CB","고덕S/S 345kV #3 M.Tr 변압기 하자점검","고덕S/S 345kV #3 M.Tr 변압기 하자점검 / #3M.Tr 2차 GIS 하자점검","2020-04-20 10:00","2020-04-22 18:00","2020-04-20 10:00","2020-04-22 18:00","연속"]
[112,"강원","동해","동해S/S STATCOM CB","2020~21년 소방설비 점검 및 보수용역","STATCOM 제어동 소방설비 종합정밀점검","2020-04-01 10:00","2020-04-01 18:00","2020-04-01 10:00","2020-04-02 18:00","연속"]
[113,"강원","동해","신제천동해#2 T/L","2020년 동해전력지사 변전정비 총액공사","1. GIS 보통점검(7271, 7200) 2. LA 보통점검 3. PT 보통점검 4. 송전선로보호반 초기점검","2020-04-02 09:00","2020-04-02 18:00","취소","취소","연속"]
[114,"강원","동해","동해S/S #3 M.Tr","2020년 동해전력지사 변전정비 협력회사 총액공사","1. 76 Bay B/F PNL 대체 2. 2차 차단기 조작시험","2020-04-20 09:30","2020-04-24 18:00","취소","취소","연속"]
[115,"강원","동해","동해삼척GP#1 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","전선접속개소 전선교체","2020-04-06 08:00","2020-04-17 18:00","2020-04-27 08:00","2020-05-08 18:00","연속"]
[116,"강원","동해","동해삼척GP#2 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","전선접속개소 전선교체","2020-04-18 08:00","2020-04-29 18:00","취소","취소","연속"]
[117,"충북","직할","신진천S/S #3 M.Tr","20-21년 충북본부 직할 변전정비회사 총액공사","#3M.Tr 보통점검","2020-04-11 09:00","2020-04-12 18:00","취소","취소","연속"]
[118,"충북","청주","세종남청주#2 T/L","345kV 세종-남청주T/L 정밀점검(20년 가공송전 위탁공사)","345kV 세종-남청주T/L 정밀점검 2020.4.6 ~4.8 : No.1~30(4회선 30기, 3일간) ※2020.4.6~4.8 : 345kV 신옥천-세종#1T/L(4회선) 병가휴전 시행 2020.4.9 ~4.11 : No.31~56(2회선 26기, 3일간) ※2020.4.11 : 154kV 남청주-오송#1T/L(4회선) 병가휴전 시행","2020-04-06 08:00","2020-04-11 18:00","2020-04-06 08:00","2020-04-08 18:00","매일"]
[119,"충북","청주","세종남청주#1 T/L","345kV 세종-남청주T/L 정밀점검(20년 가공송전 위탁공사)","345kV 세종-남청주T/L 정밀점검 2020.4.20 ~4.22 : No.1~30(4회선 30기, 3일간) ※2020.4.20~4.22 : 345kV 신옥천-세종#1T/L(4회선) 병가휴전 시행 2020.4.23 ~4.25 : No.31~56(2회선 26기, 3일간) ※2020.4.25 : 154kV 남청주-오송#2T/L(4회선) 병가휴전 시행","2020-04-20 08:00","2020-04-25 18:00","2020-04-13 08:00","2020-04-16 18:00","매일"]
[120,"충북","청주","신옥천세종#1 T/L","345kV 신옥천-세종T/L 정밀점검(20년 가공송전 위탁공사)","345kV 신옥천-세종T/L 정밀점검 2020.4.1~4.3 : No.1~48(2회선 55기, 3일간) 2020.4.6~4.8 : No.49~78(4회선 30기, 3일간) ※2020.4.6~4.11 : 345kV 세종-남청주#2T/L(4회선 병가휴전) 시행","2020-04-01 08:00","2020-04-08 18:00","2020-04-06 08:00","2020-04-09 18:00","매일"]
[121,"충북","청주","신옥천S/S #1 M.Tr","20-21년 청주전력 변전협력회사 총액공사","신옥천S/S 345kV 71BAY B/F반 대체","2020-04-01 09:30","2020-04-04 18:00","2020-04-06 09:30","2020-04-09 18:00","연속"]
[122,"충북","청주","신옥천세종#2 T/L","345kV 신옥천-세종T/L 정밀점검(20년 가공송전 위탁공사)","345kV 신옥천-세종T/L 정밀점검 2020.4.13 ~4.16 : No.1~48(2회선 55기, 3일간, 15일 공휴일 제외) 2020.4.20 ~4.22 : No.49~78(4회선 30기, 3일간) ※2020.4.20~4.25 : 345kV 세종-남청주#1T/L(4회선 병가휴전) 시행","2020-04-13 08:00","2020-04-22 18:00","2020-04-13 08:00","2020-04-16 18:00","매일"]
[123,"충북","충주","신제천S/S SVC용 M.Tr TIE CB (7200)","345kV 신제천S/S SVC 설치공사","345kV 신제천S/S SVC 회로개선 - Slow Q 제어모드 등 4항목 - 리튬이온 배터리 → 무보수 연축전지 교체공사","2020-04-06 09:00","2020-04-29 18:00","2020-04-06 09:00","2020-04-29 18:00","연속"]
[124,"충북","충주","신제천S/S #4 M.Tr","20~21년 충주 변전정비회사 총액공사","신제천 #4M.Tr A,B상 OFU 누유 보수","2020-04-01 09:30","2020-04-03 18:00","취소","취소","연속"]
[125,"충북","충주","신제천S/S SVC용 M.Tr 1차 CB (7271)","345kV 신제천S/S SVC 설치공사","345kV 신제천S/S SVC 회로개선 - Slow Q 제어모드 등 4항목 - 리튬이온 배터리 → 무보수 연축전지 교체공사","2020-04-06 09:00","2020-04-29 18:00","2020-04-06 09:00","2020-04-29 18:00","연속"]
[126,"대전충남","대전","신계룡S/S #2 M.Tr","신계룡S/S 345kV #2M.Tr 3차측 절연화 시공 및 병행작업","신계룡S/S 345kV #2M.Tr 3차측 절연화 시공 및 병행작업","2020-04-23 09:00","2020-04-24 18:00","2020-04-23 09:00","2020-04-24 18:00","연속"]
[127,"대전충남","대전","신계룡S/S #1 M.Tr","신계룡S/S 345kV #1M.Tr 3차측 절연화 시공 및 병행작업","신계룡S/S 345kV #1M.Tr 3차측 절연화 시공 및 병행작업","2020-04-21 09:00","2020-04-22 18:00","2020-04-21 09:00","2020-04-22 18:00","연속"]
[128,"대전충남","서산","당진화력S/Y 345kV 1호기 1차 CB A (7172A)","20년 서산P/O 345kV GIS 정밀점검공사","당진T/P 345kV 1호기 1차 GIS (7172) 정밀점검","2020-04-06 09:00","2020-04-10 18:00","2020-04-27 10:00","2020-05-01 18:00","연속"]
[129,"대전충남","서산","북당진현대제철 T/L","345kV 신송산분기T/L 건설사업","- 해당구간 : No.71 ~ No.69 구간내 No.70 선로 - 공사내용 : No.70 선로 가철탑 이설 전력선 공중이동 ACSR/AW 480SQ x 4B x 2C (0.793km)","2020-04-06 09:00","2020-04-09 18:00","취소","취소","연속"]
[130,"대전충남","서산","신당진개폐소현대제철 T/L","345kV 신송산분기T/L 건설공사","- 해당구간 : No.71 ~ No.69 구간내 No.70 선로 - 공사내용 : No.70 선로 가철탑 이설 전력선 공중이동 ACSR/AW 480SQ x 4B x 2C (0.793km)","2020-04-10 09:00","2020-04-13 18:00","취소","취소","연속"]
[131,"대전충남","서산","신당진S/S 345kV 7171CB#1T/L CB A (7171A)","20년 서산P/O 154kV GIS 정밀점검공사","신당진S/S 345kV 7171 GIS 정밀점검","2020-04-27 09:00","2020-05-01 18:00","취소","취소","연속"]
[132,"대전충남","서산","신서산태안TP#1 T/L","서산P/O OPGW 항공장애표시구 시설공사","신서산태안화력#1 T/L 86-88, 109-110 호간 항공구 14개 설치","2020-04-04 09:00","2020-04-04 18:00","2020-04-04 09:00","2020-04-04 18:00","연속"]
[133,"대전충남","서산","태안T/P #1 M.Tr","2020년도 서산P/O 345kV 주변압기 정밀점검 공사","태안화력 345kV #1M.Tr 정밀점검","2020-04-07 09:00","2020-04-24 18:00","2020-04-07 09:00","2020-04-24 18:00","연속"]
[134,"대전충남","서산","태안T/P 345kV #71-#72 SEC CB (71-72-0C)","현대제 345kV GIS 차단기 조작로드 교체공사","현대제 345kV GIS 차단기 조작로드 교체공사관련 무부하 가압","2020-04-23 09:00","2020-04-24 18:00","2020-04-23 09:00","2020-04-24 18:00","연속"]
[135,"대전충남","서산","태안T/P 345kV #72 BUS","현대제 345kV GIS 차단기 조작로드 교체공사","현대제 345kV GIS 차단기 조작로드 교체공사관련 무부하 가압","2020-04-23 09:00","2020-04-24 18:00","2020-04-23 09:00","2020-04-24 18:00","연속"]
[136,"대전충남","아산","아산S/S #4 M.Tr","아산S/S 345kV #4M.Tr 정밀점검공사","아산S/S 345kV #4M.Tr 정밀점검공사","2020-04-01 09:00","2020-04-10 18:00","2020-04-01 09:00","2020-04-10 18:00","연속"]
[137,"대전충남","청양","보령TP보령CC#2 T/L","보령복합 345kV보령연락#2T/L 보호반 성능개선","보령복합 345kV보령연락#2T/L 보호반 성능개선 - 보령복합 7200(보통) - 보호반 성능개선","2020-04-16 09:00","2020-04-16 18:00","2020-04-16 09:00","2020-04-16 18:00","연속"]
[138,"대전충남","청양","청양보령TP#2 T/L","345kV 송전선로 전력선 정밀점검(발전소 요청)","345kV 송전선로 전력선 정밀점검(발전소 요청)","2020-04-20 09:00","2020-04-24 16:00","취소","취소","연속"]
[139,"대전충남","청양","청양신탕정 T/L","청양S/S #73BAY B/F반 교체","청양S/S #73BAY B/F반 교체","2020-04-06 09:00","2020-04-10 18:00","2020-04-26 09:00","2020-04-30 18:00","연속"]
[140,"대전충남","청양","청양S/S #1 M.Tr","청양S/S #1M.Tr 관련설비 점검 시행","청양S/S #1M.Tr 관련설비 점검 시행 - 부싱절연유 채유 - #1M.Tr 2차 GIS 조작시험","2020-04-03 09:00","2020-04-03 18:00","2020-04-03 09:00","2020-04-03 18:00","연속"]
[141,"대전충남","청양","청양군산#2 T/L","청양S/S #73BAY B/F반 교체","청양S/S #73BAY B/F반 교체","2020-04-06 09:00","2020-04-10 18:00","2020-04-26 09:00","2020-04-30 18:00","연속"]
[142,"전북","김제","군산신김제#1 T/L","가스누기개소 보수공사","가스누기개소 보수","2020-04-09 09:00","2020-04-10 18:00","2020-04-09 09:00","2020-04-10 18:00","연속"]
[143,"전북","김제","신김제S/S 345kV #1 BUS","가스누기개소 보수공사","가스누기개소 보수","2020-04-06 09:00","2020-04-10 18:00","2020-04-06 09:00","2020-04-10 18:00","연속"]
[144,"전북","김제","신김제S/S #2 M.Tr","신김제S/S 154kV 이상 차단기 조작시험","신김제S/S 154kV 이상 차단기 조작시험","2020-04-03 10:00","2020-04-03 18:00","2020-04-03 10:00","2020-04-03 18:00","연속"]
[145,"전북","김제","신김제S/S #1 M.Tr","신김제S/S 154kV 이상 차단기 조작시험","신김제S/S 154kV 이상 차단기 조작시험","2020-04-02 10:00","2020-04-02 18:00","2020-04-02 10:00","2020-04-02 18:00","연속"]
[146,"전북","김제","신김제S/S 345kV #2 BUS","#2 BUS 가스누기 보수공사","#2 BUS 가스누기 보수공사","2020-04-20 09:00","2020-04-24 18:00","취소","취소","연속"]
[147,"전북","김제","군산신김제#1 T/L","#2 BUS 가스누기 보수공사(시험가압)","#2 BUS 가스누기 보수공사(시험가압)","2020-04-24 09:00","2020-04-24 18:00","취소","취소","연속"]
[148,"전북","직할","신옥천신남원#1 T/L","신남원S/S GAS 누기보수공사(7271/7200)","신남원S/S GAS 누기보수공사 [휴전개소 : 신옥천-신남원#1T/L, #70BUS] [작업개소 : 7271CB(B/C), 7200CB(A/B/C)]","2020-04-07 10:00","2020-04-27 18:00","2020-04-13 07:00","2020-05-13 18:00","연속"]
[149,"전북","직할","신남원S/S 345kV #70 BUS","신남원S/S GAS 누기보수공사(#70BUS)","신남원S/S GAS 누기보수공사 [휴전개소 : #70BUS] [작업개소] - 7271/7200(04/07~04/27) - 7471(05/26~05/29) - 7371(05/30~06/02) - 7671/7661(06/15~06/28)","2020-04-07 10:00","2020-04-27 18:00","취소","취소","연속"]
[150,"전북","직할","신남원S/S 345kV #75 BUS","신남원S/S GAS 누기보수공사(#75BUS)","신남원S/S GAS 누기보수공사 [휴전개소 : #75BUS] [작업개소] - 7600(04/28~05/21) - 7272(05/02~05/13) - 7352/7452(05/14~05/25) - 7500(06/03~06/14)","2020-04-28 10:00","2020-05-25 18:00","취소","취소","연속"]
[151,"전북","직할","신남원광양#2 T/L","신남원S/S GAS 누기보수공사(7600)","신남원S/S GAS 누기보수공사 [휴전개소 : 신남원-광양#2T/L, #75BUS] [작업개소 : 7600CB(C)]","2020-04-28 10:00","2020-05-01 18:00","취소","취소","연속"]
[152,"광주전남","강진","신강진광양#1 T/L","신강진-광양#1T/L GIS 초기점검","신강진-광양#1T/L GIS 초기점검 - 신강진-광양#1T/L 인출 LA 설비 개선","2020-04-29 09:00","2020-04-29 18:00","2020-04-28 09:00","2020-04-28 18:00","연속"]
[153,"광주전남","강진","신강진광양#2 T/L","신강진-광양#2T/L GIS 초기점검","신강진-광양#2T/L GIS 초기점검 - 신강진-광양#2T/L 인출 LA 설비 개선","2020-04-30 09:00","2020-04-30 18:00","2020-04-29 09:00","2020-04-29 18:00","연속"]
[154,"광주전남","광주","신광주S/S 345kV 신광주-신화순#2T/L TIE GIS","345kV 신광주S/S 345kV #1Sh.R 증설공사","사전 362GIS 기기기초를 위한 철거작업 시행","2020-04-20 09:00","2020-09-29 18:00","2020-04-20 09:00","2020-09-29 18:00","연속"]
[155,"광주전남","목포","한빛2NP한빛3NP #4 T/L","2020년 목포전력지사 362kV GIS 정밀점검공사","2020년 목포전력지사 362kV GIS 정밀점검","2020-04-24 10:00","2020-04-28 18:00","취소","취소","연속"]
[156,"광주전남","목포","신김제한빛NP#1 T/L","2020년 목포전력지사 362kV GIS 정밀점검","2020년 목포전력지사 362kV GIS 정밀점검","2020-04-06 10:00","2020-04-09 17:00","2020-04-20 10:00","2020-04-23 18:00","연속"]
[157,"광주전남","순천","신강진광양#1 T/L","광양S/S 362kV GIS 차단기 용량대체","광양S/S 362kV GIS 차단기 용량대체 -#75-#76 SEC-CB 대체(50kA - 63kA) 무부하가압 선로 휴전","2020-04-20 10:00","2020-04-21 10:00","2020-04-20 10:00","2020-04-21 10:00","연속"]
[158,"대구","경산","울주신경산#2 T/L","20-21년도 가공송전정비 협력회사 총액공사","- 전력선교체 : No.75~77, 80~82","2020-04-16 08:00","2020-04-25 18:00","2020-04-16 08:00","2020-04-25 18:00","연속"]
[159,"대구","경산","울주신경산#1 T/L","20-21년도 가공송전정비 협력회사 총액공사","- 전력선교체 : No.75~77, 80~82","2020-04-27 08:00","2020-05-06 18:00","2020-04-27 08:00","2020-05-06 18:00","연속"]
[160,"대구","칠곡","북대구S/S 345kV #1 Sh.R","북대구S/S 345kV #1Sh.R 및 7679GIS 하자점검","북대구S/S 345kV #1Sh.R 및 7679GIS 하자점검","2020-04-09 09:30","2020-04-09 18:00","2020-04-09 09:30","2020-04-09 18:00","연속"]
[161,"대구","칠곡","북대구S/S 345kV #1 Sh.R 1차 CB A (7671)","북대구S/S 345kV 7671GIS 하자점검","북대구S/S 345kV 7671GIS 하자점검","2020-04-09 09:30","2020-04-09 18:00","2020-04-09 09:30","2020-04-09 18:00","연속"]
[162,"대구","칠곡","북대구S/S 345kV 북대구-서대구#2T/L CB A (7371)","북대구S/S 345kV GIS 보통점검","북대구S/S 345kV GIS 보통점검","2020-04-10 09:30","2020-04-10 18:00","2020-04-10 09:30","2020-04-10 18:00","연속"]
[163,"대구","칠곡","서대구S/S #1 M.Tr","서대구S/S 154kV 옥외철구 설비 GIS화 공사","T-BUS 및 8DS 철거","2020-04-08 08:00","2020-04-08 18:00","2020-04-08 08:00","2020-04-08 18:00","연속"]
[164,"대구","칠곡","서대구S/S 345kV 북대구#1-선산#2T/L TIE CB A (7800)","서대구S/S 345kV GCB 공기조작부 정밀점검","서대구S/S 345kV GCB 공기조작부 정밀점검","2020-04-16 09:00","2020-04-17 18:00","2020-04-16 09:00","2020-04-17 18:00","연속"]
[165,"대구","칠곡","서대구S/S #2 M.Tr","서대구S/S 154kV 옥외철구 설비 GIS화 공사","T-BUS 및 8DS 철거","2020-04-02 08:00","2020-04-02 18:00","2020-04-02 08:00","2020-04-02 18:00","연속"]
[166,"대구","칠곡","서대구S/S 345kV 서대구-선산#1T/L CB A (7472)","서대구S/S 345kV GCB 공기조작부 정밀점검","서대구S/S 345kV GCB 공기조작부 정밀점검","2020-04-13 09:00","2020-04-14 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[167,"대구","포항","신영일S/S 345kV #3 M.Tr 1차 CB A (7572-A)","신영일SS 7500,7572 GIS 조작시험","신영일SS 7500,7572 GIS 조작시험","2020-04-13 09:00","2020-04-13 14:00","2020-04-13 09:00","2020-04-13 14:00","연속"]
[168,"대구","포항","신영일S/S 345kV #3 M.Tr 1차 TIE CB A (7500-A)","신영일SS 7500,7572 GIS 조작시험","신영일SS 7500,7572 GIS 조작시험","2020-04-13 14:00","2020-04-13 18:00","2020-04-13 14:00","2020-04-13 18:00","연속"]
[169,"대구","포항","선산신포항 T/L","345kV 신포항-북대구T/L 전력선교체공사","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-20 07:00","2020-05-05 18:00","2020-04-20 07:00","2020-05-05 18:00","연속"]
[170,"대구","포항","신포항북대구 T/L","345kV 신포항-북대구T/L 전력선교체공사","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-01 07:00","2020-04-16 18:00","2020-04-01 07:00","2020-04-16 18:00","연속"]
[171,"대구","포항","월성2N/P 345kV 월성연락#2T/L CB A (7871-A)","월성S/Y 7471 GIS 보통점검 ,7871 GIS 조작시험","월성S/Y 7471 GIS 보통점검 ,7871 GIS 조작시험","2020-04-06 14:00","2020-04-06 18:00","2020-04-06 14:00","2020-04-06 18:00","연속"]
[172,"대구","포항","월성2N/P 345kV 월성연락#1T/L CB A (7471-A)","월성S/Y 7471 GIS 보통점검 ,7871 GIS 조작시험","월성S/Y 7471 GIS 보통점검 ,7871 GIS 조작시험","2020-04-06 09:00","2020-04-06 14:00","2020-04-06 09:00","2020-04-06 14:00","연속"]
[173,"대구","칠곡","북대구S/S #1 M.Tr","북대구S/S 154kV 6144 GIS 차단부 정밀점검","북대구S/S 154kV 6144 GIS 차단부 정밀점검","2020-04-20 09:00","2020-04-21 18:00","2020-04-20 09:00","2020-04-21 18:00","연속"]
[174,"대구","칠곡","북대구S/S #2 M.Tr","북대구S/S 154kV 6244 GIS 차단부 정밀점검","북대구S/S 154kV 6244 GIS 차단부 정밀점검","2020-04-22 09:00","2020-04-23 18:00","2020-04-22 09:00","2020-04-23 18:00","연속"]
[175,"대구","칠곡","북대구S/S #3 M.Tr","북대구S/S 345kV #3M.Tr 부싱절연유 채유","북대구S/S 345kV #3M.Tr 부싱절연유 채유","2020-04-24 09:00","2020-04-24 18:00","2020-04-24 09:00","2020-04-24 18:00","연속"]
[176,"경북","구미","선산S/S #1 M.Tr","2020-21년도 구미전력지사 변전정비업체 총액공사","-7072 GIS조작시험","2020-04-20 09:00","2020-04-20 14:00","2020-04-20 09:00","2020-04-20 14:00","연속"]
[177,"경북","구미","서대구선산#2 T/L","2020년 구미전력지사 가공송전위탁회사공사","345kV 서대구-선산T/L 정밀점검 및 피뢰기 점검","2020-04-08 08:00","2020-04-09 18:00","2020-04-08 08:00","2020-04-09 18:00","매일"]
[178,"경북","구미","서대구선산#1 T/L","2020년 구미전력지사 가공송전위탁회사공사","345kV 서대구-선산T/L 정밀점검 및 피뢰기 점검","2020-04-06 08:00","2020-04-07 18:00","2020-04-06 08:00","2020-04-07 18:00","매일"]
[179,"경북","영주","신영주안동CC T/L","2020년도 가공송전 순시점검 위탁공사","345kV 신영주-안동CCT/L 송전선로 정밀점검","2020-04-20 09:00","2020-04-23 18:00","취소","취소","연속"]
[180,"경북","영주","신제천신영주#1 T/L","345kV 신제천-신영주T/L 전선접속개소 전선교체공사","○ 공사구간 : 345kV 신제천-신영주 T/L No.167-172, 181-191 ○ 전력선 교체 : ACSR 480㎟ × 4B 11.564-km","2020-04-17 07:00","2020-04-25 18:00","2020-04-17 07:00","2020-04-25 18:00","연속"]
[181,"경북","영주","신영주S/S #3 M.Tr","신영주S/S 154kV 옥외철구설비 현대화공사","170kV GIS 설치관련 부지확보공사 - 8DS 철거 및 M.Tr 인출선 6DS 직결접속 - #3M.Tr 2차측 피뢰기 이설 - #3M.Tr 3차측 GPT 이설 및 전력케이블 경로변경","2020-04-06 09:00","2020-04-13 18:00","2020-04-06 09:00","2020-04-13 18:00","연속"]
[182,"경북","영주","신영주S/S #2 M.Tr","신영주S/S 154kV 옥외철구설비 현대화공사","170kV GIS 설치관련 부지확보공사 - 8DS 철거 및 M.Tr 인출선 6DS 직결접속","2020-04-01 14:00","2020-04-01 19:00","2020-04-01 14:00","2020-04-01 19:00","연속"]
[183,"경북","영주","신영주S/S #1 M.Tr","신영주S/S 154kV 옥외철구설비 현대화공사","170kV GIS 설치관련 부지확보공사 - 8DS 철거 및 M.Tr 인출선 6DS 직결접속","2020-04-01 08:00","2020-04-01 14:00","2020-04-01 08:00","2020-04-01 14:00","연속"]
[184,"경북","영주","신영주S/S 345kV STATCOM CB A (7971-A)","2020-21년도 영주전력지사 변전정비회사 총액공사","- 7971차단기 하자점검","2020-04-06 14:00","2020-04-06 18:00","2020-04-06 14:00","2020-04-06 18:00","연속"]
[185,"경북","영주","신영주S/S 345kV STATCOM TIE CB A (7900-A)","2020-21년도 영주전력지사 변전정비회사 총액공사","- 7900차단기 하자점검","2020-04-06 09:00","2020-04-06 14:00","2020-04-06 09:00","2020-04-06 14:00","연속"]
[186,"경북","영주","신제천신영주#2 T/L","345kV 신제천-신영주T/L 전선접속개소 전선교체공사","○ 공사구간 : 345kV 신제천-신영주 T/L No.167-172, 181-191 ○ 전력선 교체 : ACSR 480㎟ × 4B 11.564-km","2020-04-26 07:00","2020-05-04 18:00","2020-04-26 07:00","2020-05-04 18:00","연속"]
[187,"경북","영주","신한울한울#2 T/L","YPP계전기 성능개선","- YPP계전기 성능개선","2020-04-07 09:00","2020-04-08 18:00","취소","취소","연속"]
[188,"경북","직할","신영일안동CC T/L","345kV 영포T/L 전선접속개소 전선교체공사","345kV 신영일-안동CC T/L 전선교체 No.147-152","2020-04-01 09:00","2020-04-09 18:00","2020-04-01 09:00","2020-04-06 18:00","연속"]
[189,"경북","직할","청송P/P 345kV #1 M.Tr 2차 GIS","20~21년 경북본부 직할 변전정비회사 총액공사","GIS 조작시험","2020-04-17 09:00","2020-04-17 18:00","취소","취소","연속"]
[190,"부산울산","동부산","고리NP S/Y 345kV 신고리-고리#1T/L-TIE CB A (7800_A)","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7800)","2020-04-23 09:30","2020-04-28 18:00","2020-04-23 09:30","2020-04-28 18:00","연속"]
[191,"부산울산","동부산","고리NP S/Y 345kV 신고리-고리#1T/L CB A (7872_A)","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7872)","2020-04-16 09:30","2020-04-21 18:00","2020-04-16 09:30","2020-04-21 18:00","연속"]
[192,"부산울산","동부산","고리2N/P 345kV #75 BUS","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7677)","2020-04-12 18:00","2020-04-13 18:00","2020-04-12 18:00","2020-04-13 18:00","연속"]
[193,"부산울산","동부산","고리NP 345kV #2 CLR CB","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7677)","2020-04-08 09:30","2020-04-13 18:00","2020-04-08 09:30","2020-04-13 18:00","연속"]
[194,"부산울산","동부산","고리2N/P 345kV #70 BUS","고리NP S/Y 현대제 362kV GIS 구조개선공사 시험가압","고리NP S/Y 현대제 362kV GIS 구조개선공사 시험가압(#70BUS)","2020-04-05 18:00","2020-04-06 18:00","2020-04-05 18:00","2020-04-06 18:00","연속"]
[195,"부산울산","동부산","고리NP 345kV #1 CLR CB","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7177)","2020-04-01 09:30","2020-04-06 18:00","2020-04-01 09:30","2020-04-06 18:00","연속"]
[196,"부산울산","동부산","고리NP S/Y 345kV 신고리-고리#2T/L-TIE CB A (7F00_A)","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7F00)","2020-04-06 09:30","2020-04-11 18:00","2020-04-06 09:30","2020-04-11 18:00","연속"]
[197,"부산울산","동부산","신양산S/S #1 M.Tr","[3차] 345kV 신양산S/S 현대화공사","1. 내용 - 신양산-신대연#2T/L 제어케이블 이설 - 345kV #1M.Tr 및 1,2,3차 제어케이블 이설 - 345kV #1M.Tr 2차 인출변경 - 154kV #61M.Tr 1차 인출변경 2. 배전선로 이설 - 8개D/L 이설","2020-04-16 09:00","2020-04-29 18:00","2020-04-16 09:00","2020-04-29 18:00","연속"]
[198,"부산울산","동부산","신양산신대연#2 T/L","[3차] 345kV 신양산S/S 현대화공사","1. 내용 - 신양산-신대연#2T/L 제어케이블 이설 - 345kV #1M.Tr 및 1,2,3차 제어케이블 이설 - 345kV #1M.Tr 2차 인출변경 - 154kV #61M.Tr 1차 인출변경 2. 배전선로 이설 - 8개D/L 이설","2020-04-16 09:00","2020-04-29 18:00","2020-04-16 09:00","2020-04-29 18:00","연속"]
[199,"부산울산","북부산","북부산S/S 345kV 서부산-북부산#2T/L CB A ((신)7971_A)","'20~21 북부산전력지사 변전정비회사 총액공사","북부산S/S 345kV 7971 GIS 하자점검 (단독차단기)","2020-04-17 10:00","2020-04-17 18:00","2020-04-17 10:00","2020-04-17 18:00","연속"]
[200,"부산울산","북부산","북부산S/S 서부산북부산 #2T/L Sh.R","'20~21 북부산전력지사 변전정비회사 총액공사","북부산S/S 345kV #2Sh.R 7977GIS 하자점검","2020-04-14 10:00","2020-04-14 18:00","2020-04-14 10:00","2020-04-14 18:00","연속"]
[201,"부산울산","울산","신온산울산TP T/L","20~21년 변전협력 총액공사","#74BAY B/F 대체","2020-04-06 09:00","2020-04-10 18:00","2020-04-06 09:00","2020-04-10 18:00","연속"]
[202,"부산울산","울산","신울산S/S 345kV 신울산-고리NP#2T/L CB A (7372_A)","20~21년 변전협력 총액공사","7372 보통점검 및 전자변 교체","2020-04-08 09:00","2020-04-08 18:00","2020-04-08 09:00","2020-04-08 18:00","연속"]
[203,"부산울산","울산","신울산S/S 345kV 고리NP#2T/L-#2 M.Tr 1차 TIE CB A (7300_A)","20~21년 변전협력 총액공사","7300 보통점검","2020-04-07 09:00","2020-04-07 18:00","2020-04-07 09:00","2020-04-07 18:00","연속"]
[204,"부산울산","울산","신울산S/S 345kV #2 M.Tr 1차 CB A (7371_A)","20~21년 변전협력 총액공사","7371 보통점검 및 전자변 교체","2020-04-06 09:00","2020-04-06 18:00","2020-04-06 09:00","2020-04-06 18:00","연속"]
[205,"부산울산","울산","신울산고리NP#1 T/L","345kV 신울산-고리NPT/L 송전용량증대전선교체공사","공사명 : 송전용량증대 전선교체공사 구간 : 42 ~ 51호, 6.662C-km 선종 : ACSR480*2B*2C => HSTACIR/AW410*2B*2C","2020-04-01 08:00","2020-04-09 18:00","취소","취소","연속"]
[206,"부산울산","울산","신울산고리NP#1 T/L","고리NP S/Y 현대제 362kV GIS 구조개선공사 시험가압","고리NP S/Y 현대제 362kV GIS 구조개선공사 시험가압(신울산-고리#1T/L)","2020-04-05 18:00","2020-04-06 18:00","2020-04-05 18:00","2020-04-06 18:00","연속"]
[207,"부산울산","울산","신울산고리NP#2 T/L","345㎸ 신울산-고리NP T/L OPGW 시설공사","345㎸ 신울산-고리NP#2T/L OPGW 25.23㎞(70SQ/48C) 시설, S/T↔ICT실간 비금속광케이블 0.7㎞ 등 부대설비 1식","2020-04-10 07:00","2020-04-23 18:00","취소","취소","연속"]
[208,"부산울산","울산","신울산S/S 345kV #5 M.Tr 1차 TIE CB A (7700_A)","20~21년 변전협력 총액공사","7700 보통점검","2020-04-02 09:00","2020-04-02 18:00","2020-04-02 09:00","2020-04-02 18:00","연속"]
[209,"부산울산","울산","신울산S/S 345kV 북부산-신울산#1T/L CB A (7471_A)","20~21년 변전협력 총액공사","7471 보통점검 및 전자변 교체","2020-04-09 09:00","2020-04-09 18:00","2020-04-09 09:00","2020-04-09 18:00","연속"]
[210,"부산울산","울산","신울산S/S 345kV #5 M.Tr 1차 CB A (7772_A)","20~21년 변전협력 총액공사","7772 보통점검","2020-04-03 09:00","2020-04-03 18:00","2020-04-03 09:00","2020-04-03 18:00","연속"]
[211,"부산울산","울산","신울산고리NP#1 T/L","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7677)","2020-04-12 18:00","2020-04-13 18:00","2020-04-12 18:00","2020-04-13 18:00","연속"]
[212,"부산울산","울산","울산C/C #3 Tie-Tr","20~21년 변전협력 총액공사","변압기 보호반 PT입력변경 6344 차단기 동작시험 및 전자변 교체","2020-04-11 09:00","2020-04-11 18:00","2020-04-11 09:00","2020-04-11 18:00","연속"]
[213,"부산울산","울산","울주고리NP#1 T/L","20년도 가공송전 순시점검 위탁공사(정밀점검)","안전거리확보(154kV 직동-반천#2T/L 휴전관련)","2020-04-08 08:00","2020-04-08 18:00","취소","취소","연속"]
[214,"부산울산","울산","울주고리NP#2 T/L","20년도 가공송전 순시점검 위탁공사(정밀점검)","안전거리확보(154kV 직동-반천#1T/L 휴전관련)","2020-04-02 08:00","2020-04-02 18:00","취소","취소","연속"]
[215,"부산울산","울산","울주고리NP#2 T/L","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선 관련 시험가압(7C71)","2020-04-10 18:00","2020-04-11 18:00","2020-04-10 18:00","2020-04-11 18:00","연속"]
[216,"부산울산","동부산","고리NP S/Y 345kV 울주-고리#2T/L CB A","고리NP S/Y 현대제 362kV GIS 구조개선공사","고리NP S/Y 현대제 362kV GIS 구조개선공사(7C71)","2020-04-06 09:30","2020-04-11 18:00","2020-04-06 09:30","2020-04-11 18:00","연속"]
[217,"부산울산","울산TP#2","울산C/C #1 Tie-Tr","154kV 자기애관 대체공사 관련 자재실측","□고장 발생 시 자기애관 폭발ㆍ비산에 의한 피해 예방 목적 애관교체공사 자재 실측 -대상 : #1,2M.Tr","2020-04-01 10:00","2020-04-01 12:00","2020-04-13 10:00","2020-04-13 12:00","연속"]
[218,"부산울산","울산TP#2","울산C/C #2 Tie-Tr","154kV 자기애관 대체공사 관련 자재실측","□고장 발생 시 자기애관 폭발ㆍ비산에 의한 피해 예방 목적 애관교체공사 자재 실측 -대상 : #1,2M.Tr","2020-04-01 13:00","2020-04-01 15:00","2020-04-13 13:00","2020-04-13 15:00","연속"]
[219,"경남","직할","신김해S/S 345kV 신김해-신녹산#1T/L CB A (7771_A)","신김해S/S 신김해-신녹산#1T/L CB(7771, 7700) 조작시험","신김해S/S 345kV 신김해-신녹산#1T/L CB(7771, 7700) 조작시험","2020-04-08 09:30","2020-04-08 13:30","2020-04-08 09:30","2020-04-08 13:30","연속"]
[220,"경남","직할","신김해S/S 345kV 신김해신녹산#1T/L-#3 M.Tr 1차 TIE CB A (7700_A)","신김해S/S 신김해-신녹산#1T/L CB(7771, 7700) 조작시험","신김해S/S 345kV 신김해-신녹산#1T/L CB(7771, 7700) 조작시험","2020-04-08 13:30","2020-04-08 17:30","2020-04-08 13:30","2020-04-08 17:30","연속"]
[221,"경남","직할","신김해S/S #3 M.Tr","신김해S/S 345kV #3M.Tr 1, 2차 LA 교체","신김해S/S 345kV #3M.Tr 1, 2차 LA 교체 및 1,2차 GIS 조작시험","2020-04-16 09:30","2020-04-17 17:30","2020-04-16 09:30","2020-04-17 17:30","연속"]
[222,"경남","진주","고령의령#1 T/L","의령S/S 345kV 고령-의령#1T/L CB(7671) 보통점검","의령S/S 345kV 고령-의령#1T/L CB(7671) 보통점검 의령S/S 345kV 고령-의령#1T/L LA(A,B,C) 보통점검","2020-04-27 10:00","2020-04-27 17:00","2020-04-27 10:00","2020-04-27 17:00","연속"]
[223,"경남","진주","고령의령#2 T/L","의령S/S 345kV 고령-의령#2T/L CB(7571) 보통점검","의령S/S 345kV 고령-의령#2T/L CB(7571) 보통점검 의령S/S 345kV 고령-의령#2T/L LA(A,B,C) 보통점검","2020-04-28 10:00","2020-04-28 17:00","2020-04-28 10:00","2020-04-28 17:00","연속"]
[224,"경남","진주","의령S/S 345kV 신남원-의령#2T/L TIE CB A (7700(A))","의령SS 345kV 신남원-의령#2TL-TIE CB(7700) 보통점검","의령SS 345kV 신남원-의령#2TL-TIE CB(7700) 보통점검","2020-04-02 10:00","2020-04-02 17:00","취소","취소","연속"]
[225,"경남","진주","의령신마산#1 T/L","의령S/S 345kV 79Bay B/F PNL 대체공사","의령S/S 345kV 79Bay B/F PNL 대체공사 [병행] 의령-신마산#1T/L CB(7971) 보통점검 [병행] 의령-신마산#1T/L-TIE CB(7900) 보통점검","2020-04-20 09:00","2020-04-24 18:00","2020-04-20 09:00","2020-04-24 18:00","연속"]
[226,"경남","진주","신남원의령#2 T/L","의령S/S 345kV 신남원-의령#2T/L CB(7771) 보통점검","의령S/S 345kV 신남원-의령#2T/L CB(7771) 보통점검 의령S/S 345kV 신남원-의령#2T/L LA(A,B,C) 보통점검","2020-04-01 10:00","2020-04-01 17:00","취소","취소","연속"]
[227,"경남","진주","의령S/S 345kV 의령-산청양수#1T/L TIE CB A (7400(A))","의령SS 345kV 의령-산청PP#1TL-TIE CB(7400) 보통점검","의령SS 345kV 의령-산청PP#1TL-TIE CB(7400) 보통점검","2020-04-02 10:00","2020-04-02 17:00","2020-04-02 10:00","2020-04-02 17:00","연속"]
[228,"경남","통영","(신)삼천포T/P 345kV 삼천포#1T/L-고성하이화력#1T/L TIE CB A (7A00_A)","(신)345kV 삼천포TIE#1T/L-고성하이#1T/L TIE 초기점검","(신)삼천포T/P 345kV 삼천포TIE#1T/L-고성하이화력#1T/L TIE GIS 초기점검(7A00)","2020-04-21 10:00","2020-04-21 18:00","2020-04-21 10:00","2020-04-21 18:00","연속"]
[229,"경남","통영","(신)삼천포T/P 345kV 고성하이화력#1T/L CB A (7A71_A)","(신)삼천포T/P 345kV 고성하이화력#1T/L GIS 초기점검","(신)삼천포T/P 345kV 고성하이화력#1T/L GIS 초기점검(7A71)","2020-04-20 10:00","2020-04-20 18:00","2020-04-20 10:00","2020-04-20 18:00","연속"]
[230,"경남","통영","(신)삼천포T/P 345kV 신마산-삼천포화력#1T/L CB A (7A72_A)","(신)삼천포T/P 345kV 신마산-삼천포화력#1T/L GIS 초기점검","(신)삼천포T/P 345kV 신마산-삼천포화력#1T/L GIS 초기점검(7A72)","2020-04-22 10:00","2020-04-22 18:00","2020-04-22 10:00","2020-04-22 18:00","연속"]
[231,"경남","통영","(신)신고성S/S 345kV #75-#76 SEC CB (신)75-76-0)","(신)신고성S/S 345kV #75-#76 SEC GIS 초기점검","(신)신고성S/S 345kV #75-#76 SEC GIS 초기점검","2020-04-29 10:00","2020-04-29 18:00","2020-04-29 10:00","2020-04-29 18:00","연속"]
[232,"경남","통영","(신)신고성S/S 345kV #70-#71 SEC CB (신)70-71-0)","(신)신고성S/S 345kV #70-#71 SEC GIS 초기점검","(신)신고성S/S 345kV #70-#71 SEC GIS 초기점검","2020-04-28 10:00","2020-04-28 18:00","2020-04-28 10:00","2020-04-28 18:00","연속"]
[233,"부산울산",null,"고리NP #2호기 주변압기 CB","고리2호기 제30차 계획예방정비 관련 주변압기/소내보조변압기(UAT) 점검\n* 조작차단기 : CB 7300, 7372","○ 고리2호기 30차 OH 345kV 계열 점검\n  - 주변압기/UAT 일반점검\n  - 주변압기/UAT 보호계전기 정기시험\n    (차단기 연동시험 포함)","2020-03-31 09:00","2020-04-13 18:00","2020-04-03 09:30","2020-04-15 18:00","연속"]
[234,"대전충남",null,"345kV 청양-보령화력 #2 T/L\n(CB 7700, 7771)","345kV 송전선로 전력선\n정밀점검","기초, 지지물, 애자․금구류, 전선 및 부대설비 등 송전설비 전반의 점검","2020-04-20 09:00","2020-04-24 16:00","취소","취소","연속"]
[235,"대전충남","서산","신당진S/S #2 M.Tr","20년 서산P/O 154kV GIS 정밀점검공사","신당진 345kV #2M.Tr 2차 GIS 정밀점검","2020-04-20 09:00","2020-04-24 18:00","2020-04-20 09:00","2020-04-24 18:00","연속"]
[236,"경남",null,"산청양수1,2호기 주변압기 CB(7100,7172,7200,7271)","자체기동발전기 예비시험","자체기동발전기 예비시험","2020-04-09 12:00","2020-04-09 14:00","2020-04-09 12:00","2020-04-09 14:00","연속"]
[237,"강원",null,"양양양수4호기 주변압기 CB(7300,7372)","#4 B급 계획예방정비공사","#4 B급 계획예방정비공사","2020-04-13 09:00","2020-04-15 09:00","2020-04-13 09:00","2020-04-15 09:00","연속"]
[238,"경남",null,"산청양수1,2호기 주변압기 CB(7100,7172,7200,7271)","자체기동발전기 예비시험","자체기동발전기 예비시험","2020-04-14 12:00","2020-04-14 14:00","2020-04-14 12:00","2020-04-14 14:00","연속"]
[239,"경북",null,"청송양수2호기 주변압기 CB(7200,7272)","#2 A급 계획예방정비공사","#2 A급 계획예방정비공사","2020-04-16 09:00","2020-04-24 18:00","2020-04-16 09:00","2020-04-24 18:00","연속"]
[240,"경남",null,"산청양수1,2호기 주변압기 CB(7100,7172,7200,7271)","자체기동발전기 예비시험","자체기동발전기 예비시험","2020-04-23 12:00","2020-04-23 14:00","2020-04-23 12:00","2020-04-23 14:00","연속"]
[241,"경남",null,"산청양수1,2호기 주변압기 CB(7100,7172,7200,7271)","자체기동발전기 예비시험","자체기동발전기 예비시험","2020-04-28 12:00","2020-04-28 14:00","2020-04-28 12:00","2020-04-28 14:00","연속"]

{"sheet":"154송부","index":3,"n_rows":538,"n_cols":13,"rows_kept":538,"cut":false,"hidden":false,"merged":[[2,0,3,0],[2,1,3,1],[2,3,3,3],[2,10,3,10],[2,4,3,4],[2,5,3,5],[2,6,2,7],[2,8,2,9],[2,12,3,12],[2,2,3,2],[2,11,3,11]]}
["2020년도 4월 휴전계획서"]
["154kV"]
["번호","1차사업소","사업소","설비명","공사명","공사개요","신청일시",null,"조정일시",null,"작업구분","연간반영\n(Y/N)","처리결과\n(Y/N)"]
[{"$nulls":6},"시작","종료","시작","종료"]
[1,"서울","중부","수색상암#1 T/L","2020년 중부P/O 170kV GIS 정밀점검(19년 이월분)","상암S/S #3M.Tr 시험가압용","2020-03-26 17:00","2020-03-26 18:00","취소","취소","연속"]
[2,"서울","성동","성수뚝도#2 T/L","'20년 성동변전정비회사 총액공사","뚝도S/S 170kV GIS 유압조작 고압호스 교체공사 - #1M.Tr 등 9Bay","2020-04-06 09:30","2020-04-06 18:00","2020-04-06 09:30","2020-04-06 18:00","연속"]
[3,"서울","성동","성수뚝도#1 T/L","'20년 성동변전정비회사 총액공사","뚝도S/S 170kV GIS 유압조작 고압호스 교체공사 - #1M.Tr 등 9Bay","2020-04-10 09:30","2020-04-10 18:00","2020-04-10 09:30","2020-04-10 18:00","연속"]
[4,"서울","성동","성동S/S 154kV #60 BUS","2020년 성동P/O 154kV GIS 정밀점검공사","성동S/S 성동군자#1T/L GIS 정밀점검 시험가압","2020-04-07 15:30","2020-04-07 17:30","2020-04-07 15:30","2020-04-07 17:30","연속"]
[5,"서울","성동","성동S/S 154kV #61 BUS","2020년 성동P/O 154kV GIS 정밀점검공사","성동S/S 성동휘경#1T/L GIS 정밀점검 시험가압","2020-04-09 15:30","2020-04-09 17:30","2020-04-09 15:30","2020-04-09 17:30","연속"]
[6,"서울","성동","성동휘경#1 T/L","2020년 성동P/O 154kV GIS 정밀점검공사","성동S/S 성동휘경#1T/L GIS 정밀점검","2020-04-08 09:30","2020-04-09 17:30","2020-04-08 09:30","2020-04-09 17:30","연속"]
[7,"서울","성동","왕십리용두 T/L","2020년 성동P/O 154kV GIS 정밀점검공사","왕십리S/S 왕십리용두T/L GIS 정밀점검","2020-04-02 09:30","2020-04-04 17:30","2020-04-02 09:30","2020-04-04 17:30","연속"]
[8,"서울","성동","화양광장 T/L","2020년 성동P/O 154kV GIS 정밀점검공사","화양S/S 화양광장T/L GIS 정밀점검","2020-04-22 09:30","2020-04-24 17:30","2020-04-22 09:30","2020-04-24 17:30","연속"]
[9,"서울","성동","미금화양 T/L","2020년 성동P/O 154kV GIS 정밀점검공사","화양S/S 미금화양T/L GIS 정밀점검","2020-04-16 09:30","2020-04-17 17:30","2020-04-27 09:30","2020-04-29 17:30","연속"]
[10,"서울","성동","화양성수 T/L","2020년 성동P/O 154kV GIS 정밀점검공사","화양S/S 화양성수T/L GIS 정밀점검","2020-04-20 09:30","2020-04-21 17:30","2020-04-20 09:30","2020-04-21 17:30","연속"]
[11,"서울","중부","순화동빙고 T/L","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #1M.Tr 1차 GIS 정밀점검","2020-04-21 17:00","2020-04-21 18:00","2020-04-21 17:00","2020-04-21 18:00","연속"]
[12,"서울","중부","동빙고S/S 154kV #60 BUS","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #1M.Tr 1차 GIS 정밀점검","2020-04-21 17:00","2020-04-21 18:00","2020-04-21 17:00","2020-04-21 18:00","연속"]
[13,"서울","중부","순화동빙고 T/L","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #2M.Tr 1차 GIS 정밀점검","2020-04-23 17:00","2020-04-23 18:00","2020-04-23 17:00","2020-04-23 18:00","연속"]
[14,"서울","중부","동빙고S/S 154kV #65 BUS","20년 중부전력지사 170kV GIS 정밀점검공사","ㅇ 동빙고S/S #2M.Tr 1차 GIS 정밀점검","2020-04-23 17:00","2020-04-23 18:00","2020-04-23 17:00","2020-04-23 18:00","연속"]
[15,"서울","중부","수색상암#2 T/L","원흥수색#2-수색상암#2TL 직결공사","원흥수색#2T/L - 수색상암#2T/L 직결","2020-04-27 08:00","2020-06-02 18:00","취소","취소","연속"]
[16,"서울","중부","양주은평#1 T/L","`20 중부P/O 변전정비회사 총액공사","은평S/S 양주은평#1T/L GIS 보통점검","2020-04-06 10:00","2020-04-06 18:00","2020-04-06 10:00","2020-04-06 18:00","연속"]
[17,"서울","중부","양주은평#2 T/L","`20 중부P/O 변전정비회사 총액공사","은평S/S 양주은평#2T/L GIS 보통점검","2020-04-07 10:00","2020-04-07 18:00","2020-04-07 10:00","2020-04-07 18:00","연속"]
[18,"서울","중부","중부S/S 154kV #61-#66 BUS TIE GIS","`20 중부P/O 변전정비회사 총액공사","중부S/S 6200 GIS 조작시험","2020-04-17 14:00","2020-04-17 18:00","2020-04-17 14:00","2020-04-17 18:00","연속"]
[19,"서울","중부","중부S/S 154kV #60-#65 BUS TIE GIS","`20 중부P/O 변전정비회사 총액공사","중부S/S 6100 GIS 조작시험","2020-04-17 10:00","2020-04-17 14:00","2020-04-17 10:00","2020-04-17 14:00","연속"]
[20,"서울","직할","지축서대문#1 T/L","20년 직할 170kV GIS 정밀점검공사","서대문S/S 지축서대문#1T/L 170kV GIS 정밀점검","2020-04-01 09:00","2020-04-02 18:00","2020-04-01 09:00","2020-04-02 18:00","연속"]
[21,"서울","직할","지축서대문#2 T/L","154kV 현저분기 지중T/L 건설공사","○공사구간 : 154KV현저변전소 ~ 154KV지축-서대문T/L 분기점 ○ 선종및 규격 : 154kV XLPE2000㎟ ○ 회선수 및 길이 : 4회선, 0.47Km","2020-04-06 09:30","2020-05-13 18:00","취소","취소","연속"]
[22,"남서울","강남","논일S/S 154kV #60 BUS","154kV 논일S/S #3M.Tr용 GIS 설치공사","154kV GIS 1CCT 설치","2020-04-22 10:00","2020-04-25 18:00","2020-04-22 10:00","2020-04-25 18:00","연속"]
[23,"남서울","강남","논일S/S 154kV #65 BUS","154kV 논일S/S #3M.Tr용 GIS 설치공사","154kV GIS 1CCT 설치","2020-04-19 10:00","2020-04-21 18:00","2020-04-19 10:00","2020-04-21 18:00","연속"]
[24,"남서울","동서울","가락동남 T/L","케이블 접속함 고열개소 보수","케이블 접속함 고열개소 보수","2020-04-08 09:00","2020-04-09 18:00","2020-04-08 09:00","2020-04-09 18:00","연속"]
[25,"남서울","동서울","강동풍납#1 T/L","170kV GIS 하자점검","170kV GIS 하자점검","2020-04-27 09:00","2020-04-27 14:00","취소","취소","연속"]
[26,"남서울","동서울","강동천호#1 T/L","170kV GIS 보통점검 및 전자변교체","170kV GIS 보통점검 및 전자변교체","2020-04-13 09:00","2020-04-13 18:00","2020-04-13 09:00","2020-04-13 18:00","연속"]
[27,"남서울","동서울","강동천호#2 T/L","170kV GIS 보통점검 및 전자변교체","170kV GIS 보통점검 및 전자변교체","2020-04-14 09:00","2020-04-14 18:00","2020-04-14 09:00","2020-04-14 18:00","연속"]
[28,"남서울","동서울","강동풍납#2 T/L","170kV GIS 하자점검","170kV GIS 하자점검","2020-04-27 14:00","2020-04-27 18:00","취소","취소","연속"]
[29,"남서울","동서울","동서울신장#1 T/L","장기사용 노후보호배전반 교체 및 170kV GIS 초기점검","동서울S/S : 보호배전반 교체 신장S/S : 170kV GIS 초기점검","2020-04-13 09:00","2020-04-16 18:00","2020-04-13 09:00","2020-04-16 18:00","연속"]
[30,"남서울","동서울","동서울신장#2 T/L","장기사용 노후보호배전반 교체 및 170kV GIS 초기점검","동서울S/S : 보호배전반 교체 신장S/S : 170kV GIS 초기점검","2020-04-27 09:00","2020-04-29 18:00","2020-04-27 09:00","2020-04-29 18:00","연속"]
[31,"남서울","동서울","동서울서종#2 T/L","170kV GCB 조작시험","170kV GCB 조작시험","2020-04-22 09:00","2020-04-22 18:00","취소","취소","연속"]
[32,"남서울","동서울","동서울서종#1 T/L","170kV GCB 조작시험","170kV GCB 조작시험","2020-04-21 09:00","2020-04-21 18:00","취소","취소","연속"]
[33,"남서울","동서울","동서울가락#2 T/L","서울 동남권지역 전기공급시설 전력구공사(동서울#2-강남5차)","전력구 흙막이 해체작업(H-Pile 인발)","2020-04-02 09:00","2020-04-02 18:00","2020-04-02 09:00","2020-04-02 18:00","연속"]
[34,"남서울","동서울","동서울강동#1 T/L","서울 동남권지역 전기공급시설 전력구공사(동서울#2-강남5차)","전력구 흙막이 해체작업(H-Pile 인발)","2020-04-04 13:00","2020-04-04 18:00","2020-04-04 13:00","2020-04-04 18:00","연속"]
[35,"남서울","동서울","동서울강동#2 T/L","서울 동남권지역 전기공급시설 전력구공사(동서울#2-강남5차)","전력구 흙막이 해체작업(H-Pile 인발)","2020-04-04 09:00","2020-04-04 13:00","2020-04-04 09:00","2020-04-04 13:00","연속"]
[36,"남서울","동서울","동서울가락#1 T/L","서울 동남권지역 전기공급시설 전력구공사(동서울#2-강남5차)","전력구 흙막이 해체작업(H-Pile 인발)","2020-04-03 09:00","2020-04-03 18:00","2020-04-03 09:00","2020-04-03 18:00","연속"]
[37,"남서울","동서울","논현선릉#2 T/L","170kV GIS 보통점검 및 전자변교체","170kV GIS 보통점검 및 전자변교체","2020-04-07 09:00","2020-04-07 18:00","2020-04-17 09:00","2020-04-17 18:00","연속"]
[38,"남서울","동서울","동서울송파#1 T/L","170kV GIS 정밀점검 및 GCB 조작시험","송파S/S 170kV GIS 정밀점검 동서울S/S 170kV GCB 조작시험","2020-04-08 14:00","2020-04-10 18:00","2020-04-08 14:00","2020-04-10 18:00","연속"]
[39,"남서울","동서울","동서울송파#2 T/L","170kV GIS 정밀점검 및 GCB 조작시험","송파S/S 170kV GIS 정밀점검 동서울S/S 170kV GCB 조작시험","2020-04-06 09:00","2020-04-08 14:00","2020-04-06 09:00","2020-04-08 14:00","연속"]
[40,"남서울","동서울","동남수서 T/L","170kV GIS 조작시험","170kV GIS 조작시험","2020-04-10 09:00","2020-04-10 18:00","2020-04-10 09:00","2020-04-10 18:00","연속"]
[41,"남서울","영등포","광명구공#3 T/L","구공S/S 170kV GIS 보통점검 및 전자변 교체","- 170kV GIS 보통점검 - 전자변 교체","2020-04-10 09:00","2020-04-10 18:00","2020-04-11 09:00","2020-04-11 18:00","연속"]
[42,"남서울","영등포","광명구공#2 T/L","구공S/S 170kV GIS 보통점검","- 차단기 개폐타임 측정 - 코일저항, 절연저항 측정 - 주도체 저항 측정 - SF6 가스 수분 및 SO2 측정 - 차단기 메커니즘 점검","2020-04-20 14:00","2020-04-20 18:00","2020-04-20 14:00","2020-04-20 18:00","연속"]
[43,"남서울","영등포","광명구공#1 T/L","구공S/S 170kV GIS 보통점검","- 차단기 개폐타임 측정 - GIS 조작시험 - 코일저항, 절연저항 측정","2020-04-20 09:00","2020-04-20 14:00","2020-04-20 09:00","2020-04-20 14:00","연속"]
[44,"남서울","영등포","독산대방#1 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험","2020-04-13 09:00","2020-04-14 18:00","취소","취소","연속"]
[45,"남서울","영등포","독산대방#2 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험","2020-04-16 09:00","2020-04-17 18:00","취소","취소","연속"]
[46,"남서울","영등포","영등포목동#2 T/L","목동S/S 170kV GIS 조작시험","- 러버히터 설치 - 차단기 개폐타임 측정 - GIS 조작시험","2020-04-13 14:00","2020-04-13 18:00","2020-04-13 14:00","2020-04-13 18:00","연속"]
[47,"남서울","영등포","영등포목동#1 T/L","목동S/S 170kV GIS 조작시험 및 전자변 교체","- 공압식 차단기 전자변 교체 - 차단기 개폐타임 측정 - GIS 조작시험","2020-04-13 09:00","2020-04-13 14:00","2020-04-13 09:00","2020-04-13 14:00","연속"]
[48,"남서울","영등포","온수소래 T/L","온수-소래T/L GIS 정밀점검공사","CB 동작시간 측정 절연저항 측정 접촉저항 측정 수분 및 SF6 가스측정 경보 및 조작시험","2020-04-01 09:00","2020-04-03 18:00","2020-04-01 09:00","2020-04-03 18:00","연속"]
[49,"남서울","영등포","천왕구로#1 T/L","2019-2020년 영등포전력지사 지중송전설비 위탁정비공사","OF케이블 절연유 채유","2020-04-16 09:00","2020-04-16 18:00","2020-04-16 09:00","2020-04-16 18:00","연속"]
[50,"남서울","영등포","천왕구로#1 T/L","2020년 영등포P/O 170kV GIS 정밀점검공사","CB 동작시간 측정 절연저항, 접촉저항 측정 수분 및 SO2 측정 GIS 내부점검 오링 및 흡습제 교체 경보 및 조작시험","2020-04-27 09:00","2020-04-28 18:00","2020-04-27 09:00","2020-04-28 18:00","연속"]
[51,"남서울","영등포","천왕구로#2 T/L","2019-2020년 영등포전력지사 지중송전설비 위탁정비공사","OF케이블 절연유 채유","2020-04-17 09:00","2020-04-17 18:00","2020-04-17 09:00","2020-04-17 18:00","연속"]
[52,"남서울","영등포","화곡S/S 154kV #60 BUS","154kV 화곡S/S 공항#2T/L GIS 정밀점검공사","- GIS(170kV 50kA 2000A) x 1CCT 정밀점검 - 기타부대공사","2020-04-18 09:00","2020-04-19 14:00","2020-04-18 09:00","2020-04-19 14:00","연속"]
[53,"남서울","영등포","화곡S/S 154kV #65 BUS","154kV 화곡S/S 공항#2T/L GIS 정밀점검공사","- GIS(170kV 50kA 2000A) x 1CCT 정밀점검 - 기타부대공사","2020-04-25 09:00","2020-04-26 14:00","2020-04-25 09:00","2020-04-26 14:00","연속"]
[54,"남서울","직할","사당봉천#2 T/L","사당-봉천#2T/L 보호배전반 교체공사","사당-봉천#2T/L 보호배전반 교체공사","2020-04-06 09:00","2020-04-08 15:00","2020-04-06 09:00","2020-04-08 15:00","연속"]
[55,"남서울","직할","사당봉천#1 T/L","사당-봉천#1T/L 선로정수 측정","사당-봉천#1T/L 선로정수 측정","2020-04-08 15:00","2020-04-08 18:00","2020-04-08 15:00","2020-04-08 18:00","연속"]
[56,"남서울","직할","신길S/S 154kV #60-#65 BUS TIE CB","주변압기 정밀점검 관련 계통 통합","신길S/S #1,2,3,4M.Tr 정밀점검 및 OLTC Diverter 교체 관련 계통 통합","2020-04-20 09:00","2020-05-15 18:00","2020-04-21 09:00","2020-05-18 18:00","연속"]
[57,"남서울","직할","양평양천#2 T/L","170kV GIS 조작시험","170kV GIS 조작시험","2020-04-09 14:00","2020-04-09 18:00","2020-04-09 14:00","2020-04-09 18:00","연속"]
[58,"남서울","직할","양평양천#1 T/L","170kV GIS 조작시험","170kV GIS 조작시험","2020-04-09 09:00","2020-04-09 14:00","2020-04-09 09:00","2020-04-09 14:00","연속"]
[59,"남서울","직할","영등포양평#1 T/L","170kV GIS 조작시험","170kV GIS 조작시험","2020-04-10 09:00","2020-04-10 14:00","2020-04-10 09:00","2020-04-10 14:00","연속"]
[60,"남서울","직할","영등포양평#2 T/L","170kV GIS 조작시험","170kV GIS 조작시험","2020-04-10 14:00","2020-04-10 18:00","2020-04-10 14:00","2020-04-10 18:00","연속"]
[61,"인천","김포","경서양촌#2 T/L","경서S/S 154kV 경서-양촌#2T/L GIS 조작시험","경서S/S 154kV 경서-양촌#2T/L GIS 조작시험","2020-04-29 10:00","2020-04-29 15:00","2020-04-29 10:00","2020-04-29 15:00","연속"]
[62,"인천","김포","경서북인천#1 T/L","경서S/S 154kV 경서-북인천#1T/L GIS 조작시험","경서S/S 154kV 경서-북인천#1T/L GIS 조작시험","2020-04-27 10:00","2020-04-27 15:00","2020-04-27 10:00","2020-04-27 15:00","연속"]
[63,"인천","김포","경서북인천#2 T/L","경서S/S 154kV 경서-북인천#2T/L GIS 조작시험","경서S/S 154kV 경서-북인천#2T/L GIS 조작시험","2020-04-28 10:00","2020-04-28 15:00","2020-04-28 10:00","2020-04-28 15:00","연속"]
[64,"인천","김포","왕길양촌#2 T/L","양촌S/S 154kV 왕길-양촌#2T/L GIS 하자점검","양촌S/S 154kV 왕길-양촌#2T/L GIS 하자점검 왕길S/S 154kV 왕길-양촌#2T/L GIS 하자점검","2020-04-07 10:00","2020-04-07 18:00","2020-04-07 10:00","2020-04-07 18:00","연속"]
[65,"인천","김포","왕길양촌#1 T/L","양촌S/S 154kV 왕길-양촌#1T/L GIS 하자점검","양촌S/S 154kV 왕길-양촌#1T/L GIS 하자점검 왕길S/S 154kV 왕길-양촌#1T/L GIS 하자점검","2020-04-06 10:00","2020-04-06 18:00","2020-04-06 10:00","2020-04-06 18:00","연속"]
[66,"인천","김포","신김포장기#1 T/L","장기S/S 154kV 신김포-장기#1T/L GIS 보통점검","장기S/S 154kV 신김포-장기#1T/L GIS 보통점검","2020-04-08 10:00","2020-04-08 18:00","2020-04-08 10:00","2020-04-08 18:00","연속"]
[67,"인천","김포","신김포장기#2 T/L","장기S/S 154kV 신김포-장기#2T/L GIS 보통점검","장기S/S 154kV 신김포-장기#2T/L GIS 보통점검","2020-04-09 10:00","2020-04-09 18:00","2020-04-09 10:00","2020-04-09 18:00","연속"]
[68,"인천","부평","관교만수#1 T/L","지중송전설비 위탁정비공사 OF케이블 절연유 열화진단","OF 케이블 절연유의 열화정도 확인","2020-04-01 09:00","2020-04-03 18:00","2020-04-01 09:00","2020-04-03 18:00","연속"]
[69,"인천","부평","송현포스코CC#1 T/L","지중송전설비 위탁정비공사 OF케이블 절연유 열화진단","OF 케이블 절연유의 열화정도 확인","2020-04-16 09:00","2020-04-17 18:00","2020-04-16 09:00","2020-04-17 18:00","연속"]
[70,"인천","부평","신가좌부개#2 T/L","154kV 신가좌-부개#2T/L 절연유 보충","154kV 신가좌-부개#2T/L 절연유 보충","2020-04-22 10:00","2020-04-22 16:00","2020-04-22 10:00","2020-04-22 16:00","연속"]
[71,"인천","부평","신가좌부개#1 T/L","154kV 신가좌-부개#1T/L 절연유 보충","154kV 신가좌-부개#1T/L 절연유 보충","2020-04-21 10:00","2020-04-21 16:00","2020-04-21 10:00","2020-04-21 16:00","연속"]
[72,"인천","부평","신경서경서#1 T/L","신경서S/S 신경서경서#1T/L 송전선로 보호반 대체","신경서S/S 신경서경서#1T/L 송전선로 보호반 대체","2020-04-06 09:00","2020-04-10 18:00","2020-04-06 09:00","2020-04-10 18:00","연속"]
[73,"인천","부평","주안S/S 154kV #65 BUS","주안S/S #2M.Tr 교체공사(무부하 가압)","1. 변압기 1BANK 철거 및 설치 2. 기타 부대공사 1식","2020-04-09 15:00","2020-04-10 15:00","2020-04-09 15:00","2020-04-10 15:00","연속"]
[74,"인천","부평","주안만수#2 T/L","주안S/S #2M.Tr 교체공사(무부하 가압)","1. 변압기 1Bank 철거 및 설치 2. 기타 부대공사 1식","2020-04-09 15:00","2020-04-10 15:00","2020-04-09 15:00","2020-04-10 15:00","연속"]
[75,"인천","시흥","신시흥남동#1 T/L","154KV 신시흥-남동#1T/L 구형 SVL 교체공사","154KV 신시흥-남동#1T/L 구형 SVL 교체공사","2020-04-24 09:00","2020-04-25 18:00","취소","취소","매일"]
[76,"인천","시흥","오봉남동#2 T/L","오봉,남동S/S 154kV 오봉남동#2T/L 보호반대체","오봉,남동S/S 154kV 오봉남동#2T/L 보호반대체","2020-04-20 10:00","2020-04-24 18:00","2020-04-20 10:00","2020-04-24 18:00","연속"]
[77,"인천","시흥","남동연수#2 T/L","154KV 남동-연수#2T/L 구형 SVL 교체공사","154KV 남동-연수#2T/L 구형 SVL 교체공사","2020-04-17 13:00","2020-04-17 18:00","2020-04-17 13:00","2020-04-17 18:00","매일"]
[78,"인천","시흥","남동연수#1 T/L","154KV 남동-연수#1T/L 구형 SVL 교체공사","154KV 남동-연수#1T/L 구형 SVL 교체공사","2020-04-17 09:00","2020-04-17 13:00","2020-04-17 09:00","2020-04-17 13:00","매일"]
[79,"인천","시흥","신시흥남동#2 T/L","154KV 신시흥-남동#2T/L 구형 SVL 교체공사","154KV 신시흥-남동#2T/L 구형 SVL 교체공사","2020-04-28 09:00","2020-04-29 18:00","취소","취소","매일"]
[80,"인천","시흥","동시화서시화 T/L","154kV 동시화-서시화T/L 구형 SVL 교체공사","154kV 동시화-서시화T/L 구형 SVL 교체공사","2020-04-16 09:00","2020-04-16 18:00","취소","취소","매일"]
[81,"인천","시흥","북시화서시화#2 T/L","서시화S/S SA혼용화공사(북시화서시화#2T/L휴전)","서시화S/S SA혼용화공사(북시화서시화#2T/L휴전)","2020-04-14 10:00","2020-04-14 18:00","2020-04-14 10:00","2020-04-14 18:00","연속"]
[82,"인천","시흥","북시화서시화#3 T/L","서시화S/S SA혼용화공사(북시화서시화#3T/L휴전)","서시화S/S SA혼용화공사(북시화서시화#3T/L휴전)","2020-04-17 10:00","2020-04-17 18:00","2020-04-17 10:00","2020-04-17 18:00","연속"]
[83,"인천","시흥","북시화서시화#1 T/L","서시화S/S SA혼용화공사(북시화서시화#1T/L휴전)","서시화S/S SA혼용화공사(북시화서시화#1T/L휴전)","2020-04-13 10:00","2020-04-13 18:00","2020-04-13 10:00","2020-04-13 18:00","연속"]
[84,"인천","직할","계양북인천 T/L","154kV계양-북인천T/L 피뢰기 설치공사","154kV계양-북인천T/L 피뢰기 설치공사","2020-04-06 08:00","2020-04-09 18:00","2020-04-06 08:00","2020-04-09 18:00","연속"]
[85,"인천","직할","임학계양#1 T/L","154kV임학-계양#1T/L 피뢰기 설치공사","154kV임학-계양#1T/L 피뢰기 설치공사","2020-04-07 08:00","2020-04-11 18:00","2020-04-07 08:00","2020-04-11 18:00","연속"]
[86,"인천","직할","임학계양#2 T/L","154kV계양-북인천T/L 피뢰기 설치공사(병가선로)","154kV계양-북인천T/L 피뢰기 설치공사 관련 병가선로 휴전","2020-04-07 08:00","2020-04-09 18:00","2020-04-07 08:00","2020-04-09 18:00","연속"]
[87,"인천","직할","계양김포#1 T/L","계양S/S 계양김포#1T/L 170kV GIS 강화조작시험","계양S/S 계양김포#1T/L 170kV GIS 강화조작시험","2020-04-17 09:30","2020-04-17 14:00","2020-04-17 09:30","2020-04-17 14:00","연속"]
[88,"인천","직할","계양김포#2 T/L","계양S/S 계양김포#2T/L 170kV GIS 강화조작시험","계양S/S 계양김포#2T/L 170kV GIS 강화조작시험","2020-04-17 14:00","2020-04-17 18:00","2020-04-17 14:00","2020-04-17 18:00","연속"]
[89,"인천","직할","임학계양#1 T/L","임학계양#1T/L 광케이블 시설공사","임학-계양S/S 광케이블 시설(OPGW 7,097km, OFC 1.764km)","2020-04-20 09:00","2020-04-24 18:00","2020-04-20 09:00","2020-04-24 18:00","연속"]
[90,"인천","직할","계양원창 T/L","임학계양#1T/L 광케이블 시설공사","임학-계양S/S 광케이블 시설(OPGW 7,097km, OFC 1.764km)","2020-04-20 09:00","2020-04-24 18:00","2020-04-20 09:00","2020-04-24 18:00","연속"]
[91,"인천","직할","고강화곡#1 T/L","고강S/S 154kV SW 증설공사(#1BUS 무부하)","고강S/S 154kV SW 증설공사(고강화곡#1T/L 이용 무부하가압) - 154kV GIS 1CCT 설치 - 기타부대공사","2020-04-06 18:00","2020-04-07 18:00","취소","취소","연속"]
[92,"인천","직할","고강S/S 154kV #1 BUS","고강S/S 154kV SW 증설공사","고강S/S 154kV SW 증설공사 - 154kV GIS 1CCT 설치 - 기타부대공사","2020-04-01 08:00","2020-04-07 18:00","2020-04-06 08:00","2020-04-10 14:00","연속"]
[93,"인천","직할","고강S/S 154kV #2 BUS","고강S/S 154kV SW 증설공사","고강S/S 154kV SW 증설공사 - 154kV GIS 1CCT 설치 - 기타부대공사","2020-04-08 08:00","2020-04-12 18:00","2020-04-10 14:00","2020-04-14 18:00","연속"]
[94,"인천","직할","고강화곡#1 T/L","고강S/S 154kV SW 증설공사(#2BUS 무부하)","고강S/S 154kV SW 증설공사(고강화곡#1T/L 이용 무부하가압) - 154kV GIS 1CCT 설치 - 기타부대공사","2020-04-11 18:00","2020-04-12 18:00","취소","취소","연속"]
[95,"인천","직할","부천원미#2 T/L","부천,원미S/S 부천원미#2T/L 170kV GIS 조작시험(양단)","부천 강화조작시험, 원미 조작시험","2020-04-03 09:30","2020-04-03 18:00","2020-04-23 09:30","2020-04-23 18:00","연속"]
[96,"인천","직할","부천원미#1 T/L","부천,원미S/S 부천원미#1T/L 170kV GIS 조작시험(양단)","부천 강화조작시험, 원미 조작시험","2020-04-02 09:30","2020-04-02 18:00","2020-04-22 09:30","2020-04-22 18:00","연속"]
[97,"인천","직할","부흥부개#1 T/L","154kV 갈산-부흥S/S SW 증설사업","154kV GIS 50kA 2,000A 2CCT(갈산 1CCT, 부흥 1CCT)","2020-04-03 18:00","2020-04-04 18:00","2020-04-03 18:00","2020-04-04 18:00","연속"]
[98,"인천","직할","신부평S/S 154kV #60 BUS","신부평S/S #61D.Tr 1차 170kV GIS 정밀 무부하가압용","신부평S/S #61D.Tr 1차 170kV GIS 정밀 무부하가압용","2020-04-25 14:00","2020-04-25 18:00","2020-04-25 14:00","2020-04-25 18:00","연속"]
[99,"인천","직할","신부평부흥#2 T/L","154kV 갈산-부흥 지중T/L 인출정비공사","○ 154kV XLPE 2,000㎟, 2C×0.2㎞(갈산-부흥)설치 및 기설선로 철거","2020-04-24 15:00","2020-05-22 18:00","2020-04-24 15:00","2020-05-22 18:00","연속"]
[100,"경기북부","고양","신파주금촌#1 T/L","154kV 신덕은-원흥/신파주-금촌T/L 계통변경공사","ㅇ 전선교체 : 신덕은-원흥T/L No.46-48 ㅇ 계탑 : No.9 ㅇ 철탑 및 암보강 : No.10 ㅇ 계통변경 : 신덕은-원흥/신파주-금촌 ⇒ 신파주-원흥/신덕은-금촌","2020-04-20 07:00","2020-04-29 18:00","2020-04-20 07:00","2020-04-29 18:00","연속"]
[101,"경기북부","고양","신파주금촌#2 T/L","154kV 신덕은-원흥/신파주-금촌T/L 계통변경공사","ㅇ 전선교체 : 신덕은-원흥T/L No.46-48 ㅇ 계탑 : No.9 ㅇ 철탑 및 암보강 : No.10 ㅇ 계통변경 : 신덕은-원흥/신파주-금촌 ⇒ 신파주-원흥/신덕은-금촌","2020-04-20 07:00","2020-04-29 18:00","2020-04-20 07:00","2020-04-29 18:00","연속"]
[102,"경기북부","고양","신파주금촌#1 T/L","154kV 신덕은-원흥/신파주-금촌T/L 계통변경공사","ㅇ 전선교체 : 신덕은-원흥T/L No.46-48 ㅇ 계탑 : No.9 ㅇ 철탑 및 암보강 : No.10 ㅇ 계통변경 : 신덕은-원흥/신파주-금촌 ⇒ 신파주-원흥/신덕은-금촌","2020-04-20 07:00","2020-04-29 18:00","취소","취소","연속"]
[103,"경기북부","고양","신파주금촌#2 T/L","154kV 신덕은-원흥/신파주-금촌T/L 계통변경공사","ㅇ 전선교체 : 신덕은-원흥T/L No.46-48 ㅇ 계탑 : No.9 ㅇ 철탑 및 암보강 : No.10 ㅇ 계통변경 : 신덕은-원흥/신파주-금촌 ⇒ 신파주-원흥/신덕은-금촌","2020-04-20 07:00","2020-04-29 18:00","취소","취소","연속"]
[104,"경기북부","고양","남면백석#1 T/L","170kV GIS 유압블럭 보수 - 제작사(동남)","남면S/S 남면-백석#1T/L 유압블럭 보수 - 제작사시공","2020-04-01 10:00","2020-04-01 18:00","2020-04-01 10:00","2020-04-01 18:00","연속"]
[105,"경기북부","고양","남면백석#1 T/L","170kV GIS 유압블럭 보수 - 제작사(동남)","남면S/S 남면-백석#1T/L 유압블럭 보수 - 제작사시공","2020-04-01 10:00","2020-04-01 18:00","취소","취소","연속"]
[106,"경기북부","고양","문발S/S 154KV #60-#65 BUS TIE GIS","2020 고양P/O 변전정비회사 총액공사(6100 BUSTIE)","170kV GIS 보통점검","2020-04-07 09:30","2020-04-07 18:00","2020-04-07 09:30","2020-04-07 18:00","연속"]
[107,"경기북부","고양","신덕은원흥#2 T/L","154kV 신덕은-원흥T/L 용량증대 전선교체공사","전력선교체 ㅇ No.39-48, 51~60 : 5.15km","2020-04-08 07:00","2020-04-29 18:00","2020-04-08 07:00","2020-04-29 18:00","연속"]
[108,"경기북부","고양","신덕은원흥#1 T/L","154kV 신덕은-원흥T/L 용량증대 전선교체공사","전력선교체 ㅇ No.39-48, 51~60 : 5.15km","2020-04-08 07:00","2020-04-29 18:00","2020-04-08 07:00","2020-04-29 18:00","연속"]
[109,"경기북부","고양","신덕은원흥#1 T/L","154kV 신덕은-원흥T/L 용량증대 전선교체공사","전력선교체 ㅇ No.39-48, 51~60 : 5.15km","2020-04-08 07:00","2020-04-29 18:00","취소","취소","연속"]
[110,"경기북부","고양","신덕은원흥#2 T/L","154kV 신덕은-원흥T/L 용량증대 전선교체공사","전력선교체 ㅇ No.39-48, 51~60 : 5.15km","2020-04-08 07:00","2020-04-29 18:00","취소","취소","연속"]
[111,"경기북부","고양","원흥수색#1 T/L","2020년 가공송전선로 순시점검 위탁공사","154kV 원흥-수색#1T/L 정밀점검","2020-04-08 07:00","2020-04-10 18:00","2020-04-08 07:00","2020-04-10 18:00","연속"]
[112,"경기북부","고양","원흥수색#2 T/L","2020년 가공송전선로 순시점검 위탁공사","154kV 원흥-수색#2T/L 정밀점검","2020-04-08 07:00","2020-04-10 18:00","2020-04-08 07:00","2020-04-10 18:00","연속"]
[113,"경기북부","고양","원흥수색#1 T/L","2020년 가공송전선로 순시점검 위탁공사","154kV 원흥-수색#1T/L 정밀점검","2020-04-08 07:00","2020-04-10 18:00","취소","취소","연속"]
[114,"경기북부","고양","원흥수색#2 T/L","2020년 가공송전선로 순시점검 위탁공사","154kV 원흥-수색#2T/L 정밀점검","2020-04-08 07:00","2020-04-10 18:00","취소","취소","연속"]
[115,"경기북부","고양","일산호수#2 T/L","2020년 고양전력지사 장기사용 170kV GIS 교체공사","일산S/S 장기사용 170kV GIS 교체공사(1CCT + PT Bay) 1. 154kV 일산S/S #2G/T 2. 154kV #60-#65 BUS PT Bay","2020-04-06 13:00","2020-04-07 13:00","2020-04-06 13:00","2020-04-07 13:00","연속"]
[116,"경기북부","고양","일산호수#2 T/L","2020년 고양전력지사 장기사용 170kV GIS 교체공사","일산S/S 장기사용 170kV GIS 교체공사(1CCT + PT Bay) 1. 154kV 일산S/S #2G/T 2. 154kV #60-#65 BUS PT Bay","2020-04-06 13:00","2020-04-07 13:00","취소","취소","연속"]
[117,"경기북부","구리","운천철원#1 T/L","2020~2021년 직할 가공송전 정비회사 총액공사","압축인류크램프 및 점퍼선 교체","2020-04-09 07:00","2020-04-09 18:00","2020-04-09 07:00","2020-04-09 18:00","연속"]
[118,"경기북부","구리","진건별내#2 T/L","'20~21 구리전력 변전정비 총액공사","진건S/S 154kV 진건-별내#2T/L GIS 하자점검공사","2020-04-23 14:00","2020-04-23 18:00","2020-04-23 14:00","2020-04-23 18:00","연속"]
[119,"경기북부","구리","진건S/S 154kV #60-#61 SEC GIS","'20~21 구리전력 변전정비 총액공사","진건S/S 154kV #60-61 SEC GIS 하자점검공사","2020-04-13 09:00","2020-04-13 14:00","2020-04-13 09:00","2020-04-13 14:00","연속"]
[120,"경기북부","구리","진건S/S 154kV #61-#66 BUS TIE GIS","'20~21 구리전력 변전정비 총액공사","진건S/S 154kV #2 BUS-TIE GIS 하자점검공사","2020-04-20 14:00","2020-04-20 18:00","2020-04-14 14:00","2020-04-14 18:00","연속"]
[121,"경기북부","구리","진건별내#1 T/L","'20~21 구리전력 변전정비 총액공사","진건S/S 154kV 진건-별내#1T/L GIS 하자점검공사","2020-04-23 09:00","2020-04-23 14:00","2020-04-23 09:00","2020-04-23 14:00","연속"]
[122,"경기북부","구리","진건S/S 154kV #60-#65 BUS TIE GIS","'20~21 구리전력 변전정비 총액공사","진건S/S 154kV #1 BUS-TIE GIS 하자점검공사","2020-04-20 09:00","2020-04-20 14:00","2020-04-14 09:00","2020-04-14 14:00","연속"]
[123,"경기북부","구리","진건S/S 154kV #65-#66 SEC GIS","'20~21 구리전력 변전정비 총액공사","진건S/S 154kV #65-66 SEC GIS 하자점검공사","2020-04-13 14:00","2020-04-13 18:00","2020-04-13 14:00","2020-04-13 18:00","연속"]
[124,"경기북부","구리","청평H/P 154kV #60-#65 BUS TIE CB","'20-21년 구리전력지사 변전정비회사 총액공사","장기사용 배전반 교체공사 - 청평H/P 154kV 모선보호반 교체공사","2020-04-20 09:00","2020-04-29 18:00","2020-04-20 09:00","2020-04-29 18:00","연속"]
[125,"경기북부","직할","백석덕계#2 T/L","2020~2021년 직할 가공송전 정비회사 총액공사","신포천-덕계#2T/L 점퍼선 교체 병가선로","2020-04-07 07:00","2020-04-07 12:00","2020-04-07 07:00","2020-04-07 12:00","연속"]
[126,"경기북부","직할","신포천덕계#2 T/L","2020~2021년 직할 가공송전 정비회사 총액공사","점퍼선 교체","2020-04-07 07:00","2020-04-07 18:00","2020-04-07 07:00","2020-04-07 18:00","연속"]
[127,"경기북부","직할","옥정송우#2 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신의정부송우T/L No.49 안전이격확보공사를 위한 하단 병가회선 휴전","2020-04-04 08:00","2020-04-04 18:00","취소","취소","연속"]
[128,"경기북부","직할","옥정송우#1 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신의정부송우T/L No.49 안전이격확보공사를 위한 하단 병가회선 휴전","2020-04-01 08:00","2020-04-01 18:00","취소","취소","연속"]
[129,"경기북부","직할","신의정부송우#2 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신설 : 1기(No.49) 철거 :2기(No.49,No.49-1) 가철탑 1기 설치 및 철거","2020-04-11 08:00","2020-04-12 18:00","취소","취소","연속"]
[130,"경기북부","직할","신의정부송우#1 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신설 : 1기(No.49) 철거 :2기(No.49,No.49-1) 가철탑 1기 설치 및 철거","2020-04-08 08:00","2020-04-10 18:00","취소","취소","연속"]
[131,"경기북부","직할","신의정부송우#2 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신설 : 1기(No.49) 철거 :2기(No.49,No.49-1) 가철탑 1기 설치 및 철거","2020-04-04 08:00","2020-04-05 18:00","취소","취소","연속"]
[132,"경기북부","직할","신의정부내촌#1 T/L","20년 직할 170kV GIS 정밀점검","- 신의정부-내촌 #1 T/L GIS 정밀점검","2020-04-13 09:00","2020-04-14 18:00","2020-04-27 09:00","2020-04-28 18:00","연속"]
[133,"경기북부","직할","신의정부송우#2 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신설 : 1기(No.49) 철거 :2기(No.49,No.49-1) 가철탑 1기 설치 및 철거","2020-04-06 08:00","2020-04-07 18:00","취소","취소","연속"]
[134,"경기북부","직할","신의정부내촌#2 T/L","20년 직할 170kV GIS 정밀점검","- 신의정부-내촌 #2 T/L GIS 정밀점검","2020-04-09 09:00","2020-04-10 18:00","취소","취소","연속"]
[135,"경기북부","직할","신의정부송우#2 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신설 : 1기(No.49) 철거 :2기(No.49,No.49-1) 가철탑 1기 설치 및 철거","2020-04-20 08:00","2020-04-21 18:00","취소","취소","연속"]
[136,"경기북부","직할","신의정부송우#1 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신설 : 1기(No.49) 철거 :2기(No.49,No.49-1) 가철탑 1기 설치 및 철거","2020-04-22 08:00","2020-04-24 18:00","취소","취소","연속"]
[137,"경기북부","직할","신의정부송우#2 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신설 : 1기(No.49) 철거 :2기(No.49,No.49-1) 가철탑 1기 설치 및 철거","2020-04-25 08:00","2020-04-26 18:00","취소","취소","연속"]
[138,"경기북부","직할","신의정부송우#1 T/L","154kV 신의정부-송우T/L No.49 안전이격거리확보공사","신설 : 1기(No.49) 철거 :2기(No.49,No.49-1) 가철탑 1기 설치 및 철거","2020-04-01 08:00","2020-04-03 18:00","취소","취소","연속"]
[139,"경기북부","직할","옥정송우#2 T/L","20년 직할 170kV GIS 정밀점검","- 옥정S/S 옥정-송우 #2 T/L GIS 정밀점검","2020-04-27 09:00","2020-04-28 18:00","2020-04-29 09:00","2020-04-30 18:00","연속"]
[140,"경기북부","직할","운천전곡#1 T/L","20년 직할 170kV GIS 정밀점검","- 전곡S/S 운천-전곡 #1 T/L GIS 정밀점검","2020-04-23 09:00","2020-04-24 18:00","2020-04-20 09:00","2020-04-21 18:00","연속"]
[141,"경기북부","직할","신포천전곡#1 T/L","20년 직할 변전정비총액공사(TL 보호반 교체)","154kV 신포천-전곡 #1T/L 보호반 1면 교체","2020-04-01 08:00","2020-04-03 18:00","2020-04-01 08:00","2020-04-03 18:00","연속"]
[142,"경기북부","직할","운천전곡#2 T/L","20년 직할 170kV GIS 정밀점검","- 전곡S/S 운천-전곡 #2 T/L GIS 정밀점검","2020-04-20 09:00","2020-04-21 18:00","2020-04-22 09:00","2020-04-23 18:00","연속"]
[143,"경기북부","직할","신포천전곡#2 T/L","20년 직할 변전정비총액공사(TL 보호반 교체)","154kV 신포천-전곡 #2T/L 보호반 1면 교체","2020-04-06 08:00","2020-04-08 18:00","2020-04-06 08:00","2020-04-08 18:00","연속"]
[144,"경기","군포","화성남양#1 T/L","남양S/S 화성-남양#1T/L GIS 조작시험","남양S/S 화성-남양#1T/L GIS 조작시험","2020-04-25 10:00","2020-04-25 14:00","2020-04-25 10:00","2020-04-25 14:00","연속"]
[145,"경기","군포","화성남양#2 T/L","남양S/S 화성-남양#2T/L GIS 조작시험","남양S/S 화성-남양#2T/L GIS 조작시험","2020-04-25 14:00","2020-04-25 18:00","2020-04-25 14:00","2020-04-25 18:00","연속"]
[146,"경기","군포","반월시화#1 T/L","반월S/S 반월-시화#1TL GIS 하자점검 및 불량패킹 재시공","반월S/S 반월-시화#1TL GIS 하자점검 및 불량패킹 재시공 / 시화S/S 반월-시화#1TL GIS 보통점검","2020-04-20 10:00","2020-04-20 14:00","2020-04-20 10:00","2020-04-20 14:00","연속"]
[147,"경기","군포","반월시화#2 T/L","반월S/S 반월-시화#2TL GIS 하자점검 및 불량패킹 재시공","반월S/S 반월-시화#2TL GIS 하자점검 및 불량패킹 재시공 / 시화S/S 반월-시화#2TL GIS 보통점검","2020-04-20 14:00","2020-04-20 18:00","2020-04-20 14:00","2020-04-20 18:00","연속"]
[148,"경기","군포","사강남양#1 T/L","사강-남양#1T/L GIS 하자점검","사강-남양#1T/L GIS 하자점검(양단)","2020-04-29 09:00","2020-04-29 14:00","2020-04-29 09:00","2020-04-29 14:00","연속"]
[149,"경기","군포","사강남양#2 T/L","사강-남양#2T/L GIS 하자점검","사강-남양#2T/L GIS 하자점검(양단)","2020-04-29 14:00","2020-04-29 18:00","2020-04-29 14:00","2020-04-29 18:00","연속"]
[150,"경기","군포","서서울산본#2 T/L","서서울S/S 서서울-산본#2T/L GIS 하자점검","서서울S/S 서서울-산본#2T/L GIS 하자점검, 산본S/S 서서울-산본#2T/L GIS 조작시험","2020-04-27 14:00","2020-04-27 18:00","2020-04-27 14:00","2020-04-27 18:00","연속"]
[151,"경기","군포","서서울산본#1 T/L","서서울S/S 서서울-산본#1T/L GIS 하자점검","서서울S/S 서서울-산본#1T/L GIS 하자점검, 산본S/S 서서울-산본#1T/L GIS 조작시험","2020-04-27 09:00","2020-04-27 14:00","2020-04-27 09:00","2020-04-27 14:00","연속"]
[152,"경기","군포","서서울남군포#2 T/L","서서울S/S 서서울-남군포#2T/L GIS 하자점검","서서울S/S 서서울-남군포#2T/L GIS 하자점검, 남군포S/S 서서울-남군포#2T/L GIS 초기점검","2020-04-29 14:00","2020-04-29 18:00","2020-04-29 14:00","2020-04-29 18:00","연속"]
[153,"경기","군포","서서울남군포#1 T/L","서서울S/S 서서울-남군포#1T/L GIS 하자점검","서서울S/S 서서울-남군포#1T/L GIS 하자점검, 남군포S/S 서서울-남군포#1T/L GIS 초기점검","2020-04-29 09:00","2020-04-29 14:00","2020-04-29 09:00","2020-04-29 14:00","연속"]
[154,"경기","군포","서서울#2서안양 T/L","154kV 서안양S/S #4M.Tr 증설공사","○#65BUS 무부하가압(24Hr) ○위상체크 및 M.Tr 무부하가압(24Hr)","2020-04-28 09:00","2020-04-30 18:00","2020-04-28 09:00","2020-04-29 18:00","연속"]
[155,"경기","군포","서서울#2서안양 T/L","154kV 서안양S/S #4M.Tr 증설공사","○ #60BUS 무부하가압(24Hr)","2020-04-24 18:00","2020-04-25 18:00","2020-04-11 09:00","2020-04-12 18:00","연속"]
[156,"경기","군포","성곡중시화 T/L","154kV 성곡-중시화T/L GIS점검(중시화 보통, 성곡 조작)","154kV 성곡-중시화T/L GIS점검(중시화 보통점검, 성곡 조작시험)","2020-04-03 08:00","2020-04-03 14:00","2020-04-03 08:00","2020-04-03 14:00","연속"]
[157,"경기","군포","시화성곡 T/L","154kV 시화-성곡T/L GIS점검(성곡 조작, 시화 조작.전자변)","154kV 시화-성곡T/L GIS점검(성곡 조작, 시화 조작 및 전자변교체)","2020-04-01 08:00","2020-04-01 18:00","2020-04-01 08:00","2020-04-01 18:00","연속"]
[158,"경기","군포","신안산남안산#1 T/L","신안산S/S 신안산-남안산#1T/L GIS 보통점검","신안산S/S 신안산-남안산#1T/L GIS 보통점검, 남안산S/S 신안산-남안산#1T/L GIS 조작시험","2020-04-07 09:00","2020-04-07 14:00","2020-04-07 09:00","2020-04-07 14:00","연속"]
[159,"경기","군포","신안산남안산#2 T/L","신안산S/S 신안산-남안산#2T/L GIS 보통점검","신안산S/S 신안산-남안산#2T/L GIS 보통점검, 남안산S/S 신안산-남안산#2T/L GIS 조작시험","2020-04-07 14:00","2020-04-07 18:00","2020-04-07 14:00","2020-04-07 18:00","연속"]
[160,"경기","군포","신안산성포#1 T/L","신안산S/S 신안산-성포#1T/L GIS 조작시험","신안산S/S 신안산-성포#1T/L GIS 조작시험, 성포S/S 신안산-성포#1T/L GIS 조작시험","2020-04-09 09:00","2020-04-09 14:00","2020-04-09 09:00","2020-04-09 18:00","연속"]
[161,"경기","군포","신안산성포#3 T/L","신안산S/S 신안산-성포#3T/L GIS 보통점검","신안산S/S 신안산-성포#3T/L GIS 보통점검, 성포S/S 신안산-성포#3T/L GIS 조작시험","2020-04-14 14:00","2020-04-14 18:00","2020-04-14 14:00","2020-04-14 18:00","연속"]
[162,"경기","군포","신안산성포#2 T/L","신안산S/S 신안산-성포#2T/L GIS 조작시험","신안산S/S 신안산-성포#2T/L GIS 조작시험, 성포S/S 신안산-성포#2T/L GIS 조작시험","2020-04-09 14:00","2020-04-09 18:00","2020-04-14 09:00","2020-04-14 14:00","연속"]
[163,"경기","군포","일동S/S 154kV #60-#65 BUS TIE GIS","일동S/S 6100 BUS TIE GIS 조작시험","일동S/S 6100 BUS TIE GIS 조작시험","2020-04-24 14:00","2020-04-24 18:00","2020-04-24 14:00","2020-04-24 18:00","연속"]
[164,"경기","군포","장덕마도 T/L","2020년 군포PO 170kV GIS 정밀점검공사-장덕SS 장덕마도TL","장덕SS 장덕마도TL GIS 정밀점검공사","2020-04-21 09:00","2020-04-24 18:00","2020-04-21 09:00","2020-04-24 18:00","연속"]
[165,"경기","군포","조암구문천#1 T/L","조암S/S 조암-구문천#1T/L GIS 조작시험","조암S/S 조암-구문천#1T/L GIS 조작시험","2020-04-01 09:00","2020-04-01 14:00","2020-04-01 09:00","2020-04-01 14:00","연속"]
[166,"경기","군포","조암구문천#2 T/L","조암S/S 조암-구문천#2T/L GIS 조작시험","조암S/S 조암-구문천#2T/L GIS 조작시험","2020-04-01 14:00","2020-04-01 18:00","2020-04-01 14:00","2020-04-01 18:00","연속"]
[167,"경기","동부","곤지암율현#2 T/L","154kV 곤지암-율현 #2T/L 송전선로 정밀점검","송전선로 정밀점검","2020-04-27 09:00","2020-04-27 18:00","취소","취소","연속"]
[168,"경기","동부","곤지암율현#1 T/L","154kV 곤지암-율현 #1T/L 송전선로 정밀점검","송전선로 정밀점검","2020-04-16 09:00","2020-04-18 18:00","취소","취소","연속"]
[169,"경기","동부","곤지암율현#1 T/L","154kV 곤지암-율현 #1T/L 불량애자교체 및 피뢰기설치공사","154kV 곤지암-율현 #1T/L 불량애자교체 및 피뢰기설치공사","2020-04-20 08:00","2020-04-20 11:00","취소","취소","연속"]
[170,"경기","동부","곤지암율현#2 T/L","154kV 곤지암-율현 #2T/L 송전선로 정밀점검","송전선로 정밀점검","2020-04-22 09:00","2020-04-24 18:00","취소","취소","연속"]
[171,"경기","동부","곤지암율현#2 T/L","154kV 곤지암-이천, 곤지암-율현 #2T/L 불량애자교체 및 피뢰기설치공사","154kV 곤지암-이천, 곤지암-율현 #2T/L 불량애자교체 및 피뢰기설치공사","2020-04-20 11:00","2020-04-21 19:00","취소","취소","매일"]
[172,"경기","동부","곤지암이천#2 T/L","154kV 곤지암-이천, 곤지암-율현 #2T/L 불량애자교체 및 피뢰기설치공사","154kV 곤지암-이천, 곤지암-율현 #2T/L 불량애자교체 및 피뢰기설치공사","2020-04-20 11:00","2020-04-21 19:00","취소","취소","매일"]
[173,"경기","동부","오포모현#1 T/L","20-21년도 송전정비 총액공사(애자교체)","154kV 오포-모현 #1T/L 국산애자 교체 - 6,14,17호","2020-04-16 07:00","2020-04-16 18:00","2020-04-16 07:00","2020-04-16 18:00","연속"]
[174,"경기","동부","오포모현#2 T/L","20-21년도 송전정비 총액공사(애자교체)","154kV 오포-모현 #2T/L 국산애자 교체 - 6,9,14,15호","2020-04-17 07:00","2020-04-17 18:00","2020-04-17 07:00","2020-04-17 18:00","연속"]
[175,"경기","동부","성현분당#2 T/L","20-21년도 송전정비 총액공사(애자교체)","154kV 분당-오포T/L 병가 구간 작업자 안전이격 확보","2020-04-13 07:00","2020-04-13 18:00","2020-04-13 07:00","2020-04-13 18:00","연속"]
[176,"경기","동부","분당오포#1 T/L","20-21년도 송전정비 총액공사(애자교체)","154kV 분당-오포#1T/L 9,26호 국산애자 교체 - 9호 전원하단 외측, 26호 전원,부하 상중하단 교체","2020-04-13 07:00","2020-04-13 18:00","2020-04-13 07:00","2020-04-13 18:00","연속"]
[177,"경기","동부","분당오포#2 T/L","20-21년도 송전정비 총액공사(애자교체)","154kV 분당-오포#2T/L 9,26호 국산애자 교체 - 분당S/S 인출, 17호 상중하단지지, 26호 전원,부하 상중하단 교체","2020-04-14 07:00","2020-04-14 18:00","2020-04-14 07:00","2020-04-14 18:00","연속"]
[178,"경기","동부","성현분당#1 T/L","20-21년도 송전정비 총액공사(애자교체)","154kV 분당-오포T/L 병가 구간 작업자 안전이격 확보","2020-04-14 07:00","2020-04-14 18:00","2020-04-14 07:00","2020-04-14 18:00","연속"]
[179,"경기","동부","산성수서#1 T/L","20년 동부 변전정비회사 총액공사","산성:산성-수서#1T/L(조작),GIS전자변교체,43L/R 회로보완 확인 및 Remote 회로분리 시행 산성-수서#2T/L(조작),GIS전자변교체,43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-04-27 09:30","2020-04-27 14:00","2020-04-27 09:30","2020-04-27 14:00","연속"]
[180,"경기","동부","산성수서#2 T/L","20년 동부 변전정비회사 총액공사","산성:산성-수서#1T/L(조작),GIS전자변교체,43L/R 회로보완 확인 및 Remote 회로분리 시행 산성-수서#2T/L(조작),GIS전자변교체,43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-04-27 14:00","2020-04-27 18:00","2020-04-27 14:00","2020-04-27 18:00","연속"]
[181,"경기","동부","성현산성#2 T/L","20년 동부 변전정비회사 총액공사","성현:산성-성현#1T/L(조작),GIS전자변교체,43L/R 회로보완 확인 및 Remote 회로분리 시행 산성-성현#2T/L(조작),GIS전자변교체,전자변 실리콘히터 설치,43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-04-29 14:00","2020-04-29 18:00","2020-04-29 14:00","2020-04-29 18:00","연속"]
[182,"경기","동부","성현산성#1 T/L","20년 동부 변전정비회사 총액공사","성현:산성-성현#1T/L(조작),GIS전자변교체,43L/R 회로보완 확인 및 Remote 회로분리 시행 산성-성현#2T/L(조작),GIS전자변교체,전자변 실리콘히터 설치,43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-04-29 09:30","2020-04-29 14:00","2020-04-29 09:30","2020-04-29 14:00","연속"]
[183,"경기","동부","이천율현#1 T/L","20년 동부 변전정비회사 총액공사","이천:이천-율현#1T/L(보통), 43L/R 회로보완 확인 및 Remote 회로분리 시행, LA(초기) 율현:이천-율현#1T/L(보통), 43L/R 회로보완 확인 및 Remote 회로분리 시행","2020-04-08 09:30","2020-04-08 18:00","2020-04-08 09:30","2020-04-08 18:00","연속"]
[184,"경기","성남","신갈S/S 154kV 기흥-신갈#1T/L GIS","신갈S/S 154kV GIS 대체","GIS 대체","2020-04-20 09:00","2020-05-07 18:00","2020-04-20 09:00","2020-05-07 18:00","연속"]
[185,"경기","성남","신성남정자 #3 T/L","효성제 GIS 토크불량개소 보수","효성제 GIS 토크불량개소 보수","2020-04-02 09:00","2020-04-02 18:00","2020-04-02 09:00","2020-04-02 18:00","연속"]
[186,"경기","성남","신성남서판교 #3 T/L","효성제 GIS 토크불량개소 보수","효성제 GIS 토크불량개소 보수","2020-04-01 09:00","2020-04-01 18:00","2020-04-01 09:00","2020-04-01 18:00","연속"]
[187,"경기","성남","신성남서판교#2 T/L","20년 성남전력지사 변전정비회사 총액공사","조작시험","2020-04-07 14:00","2020-04-07 18:00","2020-04-07 14:00","2020-04-07 18:00","연속"]
[188,"경기","성남","신용인S/S 154kV #66-#67 SEC GIS","20년 성남전력지사 변전정비회사 총액공사","조작시험","2020-04-08 09:00","2020-04-08 14:00","2020-04-08 09:00","2020-04-08 14:00","연속"]
[189,"경기","성남","신용인S/S 154kV #62-#67 BUS TIE GIS","20년 성남전력지사 변전정비회사 총액공사","조작시험","2020-04-08 14:00","2020-04-08 18:00","2020-04-08 14:00","2020-04-08 18:00","연속"]
[190,"경기","성남","신용인용인#2 T/L","154kV 신용인-용인#2T/L 송전선로 정밀점검","154kV 신용인-용인#2T/L(No.1~27) 송전선로 정밀점검","2020-04-22 09:00","2020-04-23 18:00","2020-04-22 09:00","2020-04-23 18:00","매일"]
[191,"경기","성남","신용인용인#1 T/L","154kV 신용인-용인#1T/L 송전선로 정밀점검","154kV 신용인-용인#1T/L(No.1~27) 송전선로 정밀점검","2020-04-20 09:00","2020-04-21 18:00","2020-04-20 09:00","2020-04-21 18:00","매일"]
[192,"경기","성남","정자S/S 154kV 신성남-정자#3T/L GIS","154kV 정자S/S #4M.Tr 증설사업","○ 154㎸ M.Tr 60MVA × 1Bank ○ 154㎸ GIS × 1CCT, 23㎸ GIS × 3CCT","2020-04-06 09:00","2020-04-10 13:00","2020-04-06 09:00","2020-04-10 13:00","연속"]
[193,"경기","성남","정자S/S 154kV 정자-동판교#2T/L GIS","154kV 정자S/S #4M.Tr 증설사업","○ 154㎸ M.Tr 60MVA × 1Bank ○ 154㎸ GIS × 1CCT, 23㎸ GIS × 3CCT","2020-04-09 13:00","2020-04-10 13:00","2020-04-09 13:00","2020-04-10 13:00","연속"]
[194,"경기","성남","정자S/S 154kV 정자-동판교#2T/L GIS","154kV 정자S/S #4M.Tr 증설사업","○ 154㎸ M.Tr 60MVA × 1Bank ○ 154㎸ GIS × 1CCT, 23㎸ GIS × 3CCT","2020-04-07 13:00","2020-04-08 13:00","2020-04-07 13:00","2020-04-08 13:00","연속"]
[195,"경기","직할","남수원발안#1 T/L","154kV 남수원-발안T/L OPGW 증설공사","* No.19 ~ No.37간 OP-S-S24→48 증설 6.401km * No.37 ~ 남수원G/T OP-S-L24→48 시설 6.669km * 남수원E/C ICT실 ~ G/T FOFC-S-48 시설 0.100km * 접속, 최종시험 및 기타 부대공사 1식","2020-04-11 09:00","2020-04-12 18:00","2020-04-11 09:00","2020-04-12 18:00","연속"]
[196,"경기","직할","봉담남수원#1 T/L","154kV 남수원-발안T/L OPGW 증설공사","* No.19 ~ No.37간 OP-S-S24→48 증설 6.401km * No.37 ~ 남수원G/T OP-S-L24→48 시설 6.669km * 남수원E/C ICT실 ~ G/T FOFC-S-48 시설 0.100km * 접속, 최종시험 및 기타 부대공사 1식","2020-04-01 09:00","2020-04-08 18:00","취소","취소","연속"]
[197,"경기","직할","남수원발안#2 T/L","154kV 남수원-발안T/L OPGW 증설공사","* No.19 ~ No.37간 OP-S-S24→48 증설 6.401km * No.37 ~ 남수원G/T OP-S-L24→48 시설 6.669km * 남수원E/C ICT실 ~ G/T FOFC-S-48 시설 0.100km * 접속, 최종시험 및 기타 부대공사 1식","2020-04-01 09:00","2020-04-10 18:00","취소","취소","연속"]
[198,"경기","직할","율전동수원#1 T/L","154kV 동수원S/S 현대화공사","154kV 율전-동수원#1T/L 무부하가압","2020-04-06 09:00","2020-04-06 12:00","2020-04-06 09:00","2020-04-06 12:00","연속"]
[199,"경기","직할","동안양안양CC#1 T/L","20년 직할 변전정비회사 총액공사","안열 #1T/L 조작시험","2020-04-07 09:00","2020-04-07 14:00","2020-04-07 09:00","2020-04-07 14:00","연속"]
[200,"경기","직할","동안양안양CC#2 T/L","20년 직할 변전정비회사 총액공사","안열 #2T/L 조작시험","2020-04-07 14:00","2020-04-07 18:00","2020-04-07 14:00","2020-04-07 18:00","연속"]
[201,"경기","직할","발안S/S 154kV #60 BUS","20년 직할 154kV GIS 정밀점검공사","발안-향남#1T/L DS 점검","2020-04-20 09:00","2020-04-20 19:00","취소","취소","연속"]
[202,"경기","직할","발안S/S 154kV 발안-향남#1T/L GIS","20년 직할 154kV GIS 정밀점검","발안-향남#1T/L #1,2DS 정밀점검","2020-04-20 09:00","2020-04-21 19:00","취소","취소","연속"]
[203,"경기","직할","발안구문천#1 T/L","20년 직할 154kV GIS 정밀점검공사","#4M.Tr 1차 GIS CB,DS 정밀점검 무부하가압","2020-04-29 13:00","2020-04-29 14:00","2020-04-29 13:00","2020-04-29 14:00","연속"]
[204,"경기","직할","발안구문천#1 T/L","20년 직할 154kV GIS 정밀점검공사","#4M.Tr 1차 GIS CB,DS 정밀점검 무부하가압","2020-04-28 11:00","2020-04-28 12:00","2020-04-28 11:00","2020-04-28 12:00","연속"]
[205,"경기","직할","발안S/S 154kV #60 BUS","20년 직할 154kV GIS 정밀점검공사","#4M.Tr 1차 GIS CB, DS 점검","2020-04-27 09:00","2020-04-28 12:00","취소","취소","연속"]
[206,"경기","직할","발안S/S 154kV 발안-향남#2T/L GIS","20년 직할 154kV GIS 정밀점검","발안-향남#1T/L DS 정밀점검","2020-04-22 09:00","2020-04-23 19:00","취소","취소","연속"]
[207,"경기","직할","발안S/S 154kV #60 BUS","20년 직할 154kV GIS 정밀점검공사","발안-향남#2/L DS 점검","2020-04-22 09:00","2020-04-22 19:00","취소","취소","연속"]
[208,"경기","직할","수촌조암#1 T/L","20년 직할 변전정비회사 총액공사","수촌-조암#1T/L 초기점검","2020-04-16 09:00","2020-04-16 18:00","2020-04-16 09:00","2020-04-16 18:00","연속"]
[209,"경기","직할","수촌조암#2 T/L","20년 직할 변전정비회사 총액공사","수촌-조암#2T/L 초기점검","2020-04-16 09:00","2020-04-16 18:00","2020-04-16 09:00","2020-04-16 18:00","연속"]
[210,"경기","직할","수촌S/S 154kV 화성-수촌#1T/L GIS","20년 직할 변전정비회사 총액공사","화성-수촌#1T/L GIS 초기점검","2020-04-22 09:00","2020-04-22 14:00","2020-04-22 09:00","2020-04-22 14:00","연속"]
[211,"경기","직할","수촌S/S 154kV 화성-수촌#2T/L GIS","20년 직할 변전정비회사 총액공사","화성-수촌#2T/L GIS 초기점검","2020-04-22 14:00","2020-04-22 18:00","2020-04-22 14:00","2020-04-22 18:00","연속"]
[212,"경기","직할","율전의왕#2 T/L","154kV 의왕-동안양T/L OPGW 증설공사","* No.13 ~ 의왕G/T OP-S-L24 시설 3.669km * 의왕S/S ICT실 ~ G/T FOFC-S-24 시설 0.100km * 접속, 최종시험 및 기타 부대공사 1식","2020-04-20 08:00","2020-04-23 18:00","2020-04-20 08:00","2020-04-23 18:00","연속"]
[213,"경기","직할","의왕동안양#1 T/L","154kV 의왕-동안양T/L OPGW 증설공사","* No.13 ~ 의왕G/T OP-S-L24 시설 3.669km * 의왕S/S ICT실 ~ G/T FOFC-S-24 시설 0.100km * 접속, 최종시험 및 기타 부대공사 1식","2020-04-20 08:00","2020-04-23 18:00","2020-04-20 08:00","2020-04-23 18:00","연속"]
[214,"경기","직할","평촌안양2CC#3 T/L","2019년 평촌S/S 23kV 장기사용 GIS 대체공사","SA 혼용반 케이블 이설 공사","2020-04-01 09:00","2020-04-01 18:00","2020-04-01 09:00","2020-04-01 18:00","연속"]
[215,"경기","직할","안양평촌#1 T/L","2019년 평촌S/S 23kV 장기사용 GIS 대체공사","SA 혼용반 케이블 이설 공사","2020-04-08 09:00","2020-04-08 18:00","2020-04-08 09:00","2020-04-08 18:00","연속"]
[216,"경기","직할","관양평촌#2 T/L","2019년 평촌S/S 23kV 장기사용 GIS 대체공사","SA 혼용반 케이블 이설 공사","2020-04-16 09:00","2020-04-16 18:00","2020-04-16 09:00","2020-04-16 18:00","연속"]
[217,"경기","직할","관양평촌#1 T/L","2019년 평촌S/S 23kV 장기사용 GIS 대체공사","SA 혼용반 케이블 이설 공사","2020-04-24 09:00","2020-04-24 18:00","2020-04-24 09:00","2020-04-24 18:00","연속"]
[218,"경기","직할","평촌안양2CC#1 T/L","2019년 평촌S/S 23kV 장기사용 GIS 대체공사","SA 혼용반 케이블 이설 공사","2020-04-03 09:00","2020-04-03 18:00","2020-04-03 09:00","2020-04-03 18:00","연속"]
[219,"경기","직할","평촌안양2CC#2 T/L","2019년 평촌S/S 23kV 장기사용 GIS 대체공사","SA 혼용반 케이블 이설 공사","2020-04-02 09:00","2020-04-02 18:00","2020-04-02 09:00","2020-04-02 18:00","연속"]
[220,"경기","직할","안양평촌#2 T/L","2019년 평촌S/S 23kV 장기사용 GIS 대체공사","SA 혼용반 케이블 이설 공사","2020-04-07 09:00","2020-04-07 18:00","2020-04-07 09:00","2020-04-07 18:00","연속"]
[221,"경기","직할","발안향남#2 T/L","154kV 남수원-발안T/L OPGW 증설공사","* No.19 ~ No.37간 OP-S-S24→48 증설 6.401km * No.37 ~ 남수원G/T OP-S-L24→48 시설 6.669km * 남수원E/C ICT실 ~ G/T FOFC-S-48 시설 0.100km * 접속, 최종시험 및 기타 부대공사 1식","2020-04-11 09:00","2020-04-12 18:00","2020-04-11 09:00","2020-04-12 18:00","연속"]
[222,"경기","평택","고덕진위#2 T/L","154kV 고덕-진위T/L 정밀점검","154kV 고덕-진위T/L 정밀점검 - 점검대상 : 154kV 고덕-진위T/L 철탑 42기 - 점검일정 : #1T/L 3/23~25, #2T/L 3/26~28","2020-04-23 09:00","2020-04-25 18:00","2020-04-23 09:00","2020-04-25 18:00","연속"]
[223,"경기","평택","고덕진위#1 T/L","154kV 고덕-진위T/L 정밀점검","154kV 고덕-진위T/L 정밀점검 - 점검대상 : 154kV 고덕-진위T/L 철탑 42기 - 점검일정 : #1T/L 3/23~25, #2T/L 3/26~28","2020-04-20 09:00","2020-04-22 18:00","2020-04-20 09:00","2020-04-22 18:00","연속"]
[224,"경기","평택","고덕평택#1 T/L","154kV 동평택S/S 건설사업","154kV 동평택S/S 변전설비 최초가압","2020-04-29 13:00","2020-04-30 13:00","2020-04-29 13:00","2020-04-30 13:00","연속"]
[225,"경기","평택","송탄오성CC#1 T/L","154kV 송탄-오성CCT/L 14호 지장철탑 이설공사","고덕산단진입도로 개설관련 지장철탑 이설공사 1기 신설, 1기 철거, 1기 임시, 0.553km","2020-04-06 07:00","2020-04-08 18:00","2020-04-06 07:00","2020-04-08 18:00","연속"]
[226,"경기","평택","송탄오성CC#2 T/L","154kV 송탄-오성CCT/L 14호 지장철탑 이설공사","고덕산단진입도로 개설관련 지장철탑 이설공사 1기 신설, 1기 철거, 1기 임시, 0.553km","2020-04-09 07:00","2020-04-11 18:00","2020-04-09 07:00","2020-04-11 18:00","연속"]
[227,"경기","평택","원정평택T/P#2 T/L","원정S/S 154kV 원정-평택T/P#2T/L GIS 보통점검","원정S/S 154kV 원정-평택T/P#2T/L GIS 보통점검","2020-04-14 10:00","2020-04-14 18:00","2020-04-14 10:00","2020-04-14 18:00","연속"]
[228,"경기","평택","원정평택T/P#1 T/L","원정S/S 154kV 원정-평택T/P#1T/L GIS 보통점검","원정S/S 154kV 원정-평택T/P#1T/L GIS 보통점검","2020-04-13 10:00","2020-04-13 18:00","2020-04-13 10:00","2020-04-13 18:00","연속"]
[229,"경기","평택","포승청북 T/L","포승S/S 154kV 포승-청북T/L GIS 정밀점검","포승S/S 154kV 포승-청북T/L GIS 정밀점검 / 청북S/S 154kV 포승-청북T/L GIS 보통점검","2020-04-27 09:00","2020-04-29 18:00","2020-04-27 09:00","2020-04-29 18:00","연속"]
[230,"경기","평택","만호청북#1 T/L","청북S/S 154kV 만호-청북T/L GIS 보통점검","청북S/S 154kV 만호-청북T/L GIS 보통점검","2020-04-17 10:00","2020-04-17 18:00","2020-04-17 10:00","2020-04-17 18:00","연속"]
[231,"경기","평택","청북평택#2 T/L","청북S/S 154kV 청북-평택#2T/L GIS 보통점검","청북S/S 154kV 청북-평택#2T/L GIS 보통점검","2020-04-16 10:00","2020-04-16 18:00","2020-04-16 10:00","2020-04-16 18:00","연속"]
[232,"경기","평택","청북평택#1 T/L","청북,평택S/S 154kV 청북-평택#1T/L GIS,GCB 보통점검","청북,평택S/S 154kV 청북-평택#1T/L GIS,GCB 보통점검","2020-04-03 10:00","2020-04-03 18:00","2020-04-03 10:00","2020-04-03 18:00","연속"]
[233,"경기","평택","평택추팔#1 T/L","평택S/S 154kV 평택-추팔#1T/L GCB 정밀점검","평택S/S 154kV 평택-추팔#1T/L GCB 정밀점검 / 추팔S/S 154kV 평택-추팔#1T/L GIS 보통점검","2020-04-20 09:00","2020-04-22 18:00","2020-04-20 09:00","2020-04-22 18:00","연속"]
[234,"경기","평택","평택TP평택CC#2 T/L","평택C/C 154kV 평택복합#2T/L GIS 보통점검 / 전자변 교체","평택C/C 154kV 평택복합#2T/L GIS 보통점검 / 전자변 교체","2020-04-23 10:00","2020-04-23 18:00","2020-04-23 10:00","2020-04-23 18:00","연속"]
[235,"경기","평택","평택TP평택CC#1 T/L","평택C/C 154kV 평택복합#1T/L GIS 보통점검 / 전자변 교체","평택C/C 154kV 평택복합#1T/L GIS 보통점검 / 전자변 교체","2020-04-22 10:00","2020-04-22 18:00","2020-04-22 10:00","2020-04-22 18:00","연속"]
[236,"경기","평택","포승평택TP#1 T/L","20-21 송전정비회사총액공사(전력선교체)","전력선 교체(7호 ~10호, 14호 ~ 18호)","2020-04-20 07:00","2020-04-25 18:00","2020-04-20 07:00","2020-04-25 18:00","연속"]
[237,"경기","동부","곤지암이천#1 T/L","154kV 곤지암-율현 #1T/L 불량애자교체 및 피뢰기설치공사 안전이격","154kV 곤지암-율현 #1T/L 불량애자교체 및 피뢰기설치공사 안전이격","2020-04-20 08:00","2020-04-20 11:00","취소","취소","연속"]
[238,"경기","평택","포승평택TP#2 T/L","포승-평택T/P #2T/L GIS 정밀점검","포승-평택T/P #2T/L GIS 정밀점검","2020-04-27 09:00","2020-04-29 18:00","2020-04-27 09:00","2020-04-29 18:00","연속"]
[239,"강원","동해","도계태백 T/L","2020년 동해전력지사 170kV GIS 정밀점검","1. GIS 정밀점검 2. LA 보통점검","2020-04-06 09:00","2020-04-08 18:00","2020-04-06 09:00","2020-04-08 18:00","연속"]
[240,"강원","동해","이원도계 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","활선애자청소","2020-04-02 08:00","2020-04-02 18:00","취소","취소","연속"]
[241,"강원","동해","이원태백 T/L","2020-21년 동해전력지사 송전정비회사 총액공사","활선애자청소","2020-04-01 08:00","2020-04-01 18:00","2020-04-02 08:00","2020-04-02 18:00","연속"]
[242,"강원","원주","홍천남춘천 T/L","2020년 원주전력지사 변전정비 총액공사","- 170kV GIS 보통점검","2020-04-03 10:00","2020-04-03 18:00","2020-04-03 10:00","2020-04-03 18:00","연속"]
[243,"강원","원주","홍천상남#1 T/L","2020년 원주전력지사 변전정비 총액공사","- 170kV GIS 보통점검 - LA 보통점검(도블시험)","2020-04-06 10:00","2020-04-06 18:00","2020-04-06 10:00","2020-04-06 18:00","연속"]
[244,"강원","원주","홍천상남#2 T/L","2020년 원주전력지사 변전정비 총액공사","- 170kV GIS 보통점검 - LA 보통점검(도블시험)","2020-04-07 10:00","2020-04-07 18:00","2020-04-07 10:00","2020-04-07 18:00","연속"]
[245,"강원","직할","상남인제#2 T/L","2020~2021년 강원지역본부 직할 변전정비 총액공사","인제S/S 154kV 상남-인제 #2 T/L 피뢰기 점검","2020-04-22 10:00","2020-04-22 14:00","취소","취소","연속"]
[246,"강원","직할","철원화천#1 T/L","2020년 가공송전 위탁공사(정밀점검)","154kV 철원-화천T/L 정밀점검(106기) (주말기간 작업 미시행)","2020-04-06 09:00","2020-04-15 18:00","취소","취소","매일"]
[247,"강원","직할","철원화천#2 T/L","2020년 가공송전 위탁공사(정밀점검)","154kV 철원-화천T/L 정밀점검(106기) (주말기간 작업 미시행)","2020-04-16 09:00","2020-04-27 18:00","취소","취소","매일"]
[248,"강원","직할","화천화천HP#2 T/L","2020년 가공송전 위탁공사(정밀점검)_4회선 안전확보","154kV 철원화천T/L 정밀점검(안전확보) 4회선구간 안전확보를 위한 상단구간 휴전","2020-04-27 09:00","2020-04-27 18:00","취소","취소","연속"]
[249,"강원","직할","화천화천HP#1 T/L","2020년 가공송전 위탁공사(정밀점검)_4회선 안전확보","154kV 철원화천T/L 정밀점검(안전확보) 4회선구간 안전확보를 위한 상단구간 휴전","2020-04-15 09:00","2020-04-15 18:00","취소","취소","연속"]
[250,"강원","강릉","속초S/S #1 EM.Tr CB","ESS 배터리 소화설비 설치공사","ESS 배터리 소화설비 설치공사(현재 운전정지 중)","2020-04-20 10:00","2020-05-08 18:00","2020-04-20 10:00","2020-05-08 18:00","연속"]
[251,"충북","직할","진천광혜원#2 T/L","광혜원S/S 154kV 장기사용 GIS 대체공사","#1M.Tr 부싱 조립 및 신규 GIS 가압","2020-04-27 09:00","2020-04-30 18:00","취소","취소","연속"]
[252,"충북","직할","서운광혜원 T/L","광혜원S/S 154kV 장기사용 GIS 대체공사","#2M.Tr 부싱조립 및 신규 GIS 가압","2020-04-21 09:00","2020-04-26 18:00","2020-04-20 09:00","2020-04-24 18:00","연속"]
[253,"충북","직할","진천광혜원#1 T/L","2020~21년 직할 송전정비회사 총액공사","불량애자교체(진천s/s, No.3), 압축인류클램프교체(광혜원s/s), 조류착지방지방치(No.1~43)","2020-04-21 08:00","2020-04-25 18:00","2020-04-20 08:00","2020-04-24 18:00","매일"]
[254,"충북","직할","신진천S/S 154kV #65 BUS","20-21년 충북본부 직할 변전정비회사 총액공사","#65BUS 철공진방지장치 회로개선 및 모선보호반 대체","2020-04-07 09:00","2020-04-10 18:00","2020-04-07 09:00","2020-04-10 18:00","연속"]
[255,"충북","청주","남청주죽림#2 T/L","154kV 남청주-죽림T/L OPGW 시설공사","154kV 남청주-죽림T/L 가공지선 철거 및 OPGW 7km 시설","2020-04-11 09:00","2020-04-12 18:00","2020-04-11 09:00","2020-04-12 18:00","연속"]
[256,"충북","청주","남청주오송#1 T/L","154kV 남청주-오송T/L 정밀점검(20년 가공송전 위탁공사)","154kV 남청주-오송T/L 4회선 1기(No.5) 정밀점검 ※ 2020.4.11 345kV 세종-남청주#2T/L(4회선 병행)휴전 시행","2020-04-11 08:00","2020-04-11 18:00","취소","취소","연속"]
[257,"충북","청주","남청주죽림#2 T/L","154kV 남청주-죽림T/L OPGW 시설공사","154kV 남청주-죽림T/L 가공지선 철거 및 OPGW 7km 시설","2020-04-04 09:00","2020-04-05 18:00","2020-04-04 09:00","2020-04-05 18:00","연속"]
[258,"충북","청주","남청주오송#2 T/L","154kV 남청주-오송T/L 정밀점검(20년 가공송전 위탁공사)","154kV 남청주-오송T/L 4회선 1기(No.5) 정밀점검 ※ 2020.4.25 345kV 세종-남청주#1T/L(4회선 병행)휴전 시행","2020-04-25 08:00","2020-04-25 18:00","취소","취소","연속"]
[259,"충북","청주","북청주봉명#1 T/L","2020년 청주전력지사 170kV GIS 정밀점검","2020년 청주전력지사 170kV GIS 정밀점검","2020-04-23 09:00","2020-04-25 18:00","2020-04-27 09:00","2020-04-29 18:00","연속"]
[260,"충북","청주","북청주봉명#2 T/L","2020년 청주전력지사 170kV GIS 정밀점검","2020년 청주전력지사 170kV GIS 정밀점검","2020-04-27 09:00","2020-04-29 18:00","취소","취소","연속"]
[261,"충북","청주","사직북청주#1 T/L","20-21년 청주전력 변전정비회사 총액공사","사직S/S,북청주S/S 154kV 사직-북청주#1T/L 보호반 대체","2020-04-20 09:30","2020-04-24 18:00","2020-04-18 09:00","2020-04-19 18:00","연속"]
[262,"충북","청주","서청주사직#1 T/L","20-21년 청주전력 변전정비회사 총액공사","서청주S/S,사직S/S 서청주-사직#1T/L 154kV GIS 보통점검","2020-04-26 09:30","2020-04-26 18:00","2020-04-26 09:30","2020-04-26 18:00","연속"]
[263,"충북","청주","서청주사직#2 T/L","20-21년 청주전력 변전정비회사 총액공사","서청주,사직S/S 154kV 서청주-사직#2T/L 보호반 대체","2020-04-30 09:30","2020-05-03 18:00","2020-04-30 09:30","2020-05-01 18:00","연속"]
[264,"충북","청주","옥천영동 T/L","2020년 청주전력지사 170kV GIS 정밀점검","2020년 청주전력지사 170kV GIS 정밀점검","2020-04-04 09:00","2020-04-05 18:00","2020-04-04 09:00","2020-04-05 18:00","연속"]
[265,"충북","청주","상주영동 T/L","2020년 청주전력지사 170kV GIS 정밀점검","2020년 청주전력지사 170kV GIS 정밀점검","2020-04-11 09:00","2020-04-12 18:00","2020-04-11 09:00","2020-04-12 18:00","연속"]
[266,"충북","청주","오송북청주#2 T/L","154kV 국사-봉명T/L 안전이격확보공사","154kV 오송-북청주#2TL 충전부 방호조치","2020-04-30 07:00","2020-04-30 18:00","취소","취소","연속"]
[267,"충북","충주","금왕남음성#2 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","정밀점검 (No.42, 남음성S/S)","2020-04-30 08:00","2020-04-30 18:00","취소","취소","매일"]
[268,"충북","충주","금왕남음성#1 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","정밀점검 (No.42, 남음성S/S)","2020-04-29 08:00","2020-04-29 18:00","2020-04-27 11:00","2020-04-27 18:00","매일"]
[269,"충북","충주","남음성덕산#1 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","정밀점검 (남음성S/S~덕산S/S)","2020-04-30 08:00","2020-05-02 18:00","2020-04-28 08:00","2020-04-29 18:00","매일"]
[270,"충북","충주","남음성덕산#2 T/L","2020년 직할 가공송전선로 순시점검 위탁공사","정밀점검 (남음성S/S~덕산S/S)","2020-04-27 08:00","2020-04-29 18:00","2020-04-27 08:00","2020-04-27 11:00","매일"]
[271,"충북","충주","신제천왕암#1 T/L","2020-2021년 송전정비회사 총액공사","철탑 도장 (No.14,21,25)","2020-04-06 08:00","2020-04-08 18:00","2020-04-04 08:00","2020-04-05 18:00","매일"]
[272,"충북","충주","신제천제천#2 T/L","2020-2021년 송전정비회사 총액공사","철탑도장(No.14,21,25)","2020-04-09 08:00","2020-04-11 18:00","2020-04-11 08:00","2020-04-12 18:00","매일"]
[273,"충북","충주","신제천왕암#2 T/L","2020-2021년 송전정비회사 총액공사","철탑도장(No.14,21,25)","2020-04-09 08:00","2020-04-11 18:00","2020-04-11 08:00","2020-04-12 18:00","매일"]
[274,"충북","충주","신제천제천#1 T/L","2020-2021년 송전정비회사 총액공사","철탑도장(No.14,21,25)","2020-04-06 08:00","2020-04-08 18:00","2020-04-04 08:00","2020-04-05 18:00","매일"]
[275,"충북","충주","왕암충주 T/L","'20-21년 충주전력지사 변전정비 총액공사","왕암S/S 왕암-충주T/L GIS 보통점검","2020-04-23 10:00","2020-04-23 18:00","취소","취소","연속"]
[276,"충북","충주","왕암북충주 T/L","'20-21년 충주전력지사 변전정비 총액공사","왕암S/S 왕암-북충주T/L GIS 보통점검","2020-04-24 10:00","2020-04-24 18:00","2020-04-24 10:00","2020-04-24 18:00","연속"]
[277,"충북","충주","왕암가남#2 T/L","'20-21년 충주전력지사 변전정비 총액공사","왕암S/S 왕암-가남#2T/L GIS 보통점검","2020-04-28 10:00","2020-04-28 18:00","취소","취소","연속"]
[278,"충북","충주","왕암가남#1 T/L","'20-21년 충주전력지사 변전정비 총액공사","왕암S/S 왕암-가남#1T/L GIS 보통점검","2020-04-27 10:00","2020-04-27 18:00","취소","취소","연속"]
[279,"충북","충주","제천영월#2 T/L","'20-21년 충주전력지사 변전정비 총액공사","제천S/S 제천-영월#2T/L GIS 보통점검","2020-04-17 09:00","2020-04-17 18:00","2020-04-17 09:00","2020-04-17 18:00","연속"]
[280,"충북","충주","제천영월#1 T/L","'20-21년 충주전력지사 변전정비 총액공사","제천S/S 제천-영월#1T/L GIS 보통점검","2020-04-16 09:00","2020-04-16 18:00","2020-04-16 09:00","2020-04-16 18:00","연속"]
[281,"충북","청주","남청주청주#3 T/L","20-21년 청주전력 변전정비회사 총액공사","남청주,청주S/S 남청주-청주#3T/L 154kV GIS 하자점검","2020-04-09 09:30","2020-04-09 18:00","취소","취소","연속"]
[282,"충북","청주","남청주청주#2 T/L","20-21년 청주전력 변전정비회사 총액공사","청주S/S 남청주-청주#2T/L 154kV GIS 초기점검","2020-04-13 09:30","2020-04-13 18:00","2020-04-13 09:30","2020-04-13 18:00","연속"]
[283,"대전충남","서산","석문당진화력#1 T/L","당진화력S/Y 154kV 장기사용 GIS 대체공사","154kV GIS * 1CCT 교체","2020-04-16 09:00","2020-04-22 18:00","취소","취소","연속"]
[284,"대전충남","서산","석문당진화력#2 T/L","당진화력S/Y 154kV 장기사용 GIS 대체공사","154kV GIS * 1CCT 교체","2020-04-23 09:00","2020-04-29 18:00","취소","취소","연속"]
[285,"대전충남","서산","대산석문#2 T/L","20년 서산P/O 변전정비 총액공사","대산S/S 154kV 대산-석문#2T/L LA 보통점검","2020-04-02 09:00","2020-04-02 18:00","2020-04-02 09:00","2020-04-02 18:00","연속"]
[286,"대전충남","서산","대산석문#1 T/L","20년 서산P/O 변전정비 총액공사","대산S/S 154kV 대산-석문#1T/L LA,CVT 보통점검","2020-04-01 09:00","2020-04-01 18:00","2020-04-01 09:00","2020-04-01 18:00","연속"]
[287,"대전충남","서산","신당진S/S 345kV #1 M.Tr 2차 CB","20년 서산P/O 154kV GIS 정밀점검공사","신당진 345kV #1M.Tr 2차 GIS 정밀점검","2020-04-06 09:00","2020-04-10 18:00","취소","취소","연속"]
[288,"대전충남","서산","신당진S/S 345kV #2 M.Tr 2차 CB","20년 서산P/O 154kV GIS 정밀점검공사","신당진 345kV #2M.Tr 2차 GIS 정밀점검","2020-04-20 09:00","2020-04-24 18:00","취소","취소","연속"]
[289,"대전충남","세종","세종송강#2 T/L","[송전] 154kV 세종-송강T/L 안전이격확보공사","ㅇ 공사구간 : 154kV 세종-송강T/L No.17~19 ㅇ 철탑 : No.18호 1기 설치, 가철주 1기 ㅇ 전력선 : HSTACIR/AW 330 x S x 2C (0.25km) 교체(No.18~19)","2020-04-27 07:00","2020-04-30 18:00","취소","취소","연속"]
[290,"대전충남","아산","장재불당#1 T/L","불당S/S 154kV 장재-불당#1T/L GIS 전자변 교체","불당S/S 154kV 장재-불당#1T/L GIS 전자변 교체","2020-04-13 09:00","2020-04-13 18:00","2020-04-13 09:00","2020-04-13 18:00","연속"]
[291,"대전충남","아산","신탕정탕정#2 T/L","신탕정,탕정S/S 154lV 신탕정-탕정#2T/L GIS 보통점검","신탕정,탕정S/S 154lV 신탕정-탕정#2T/L GIS 보통점검","2020-04-22 09:00","2020-04-22 18:00","취소","취소","연속"]
[292,"대전충남","아산","신탕정탕정#1 T/L","신탕정,탕정S/S 154lV 신탕정-탕정#1T/L GIS 보통점검","신탕정,탕정S/S 154lV 신탕정-탕정#1T/L GIS 보통점검","2020-04-21 09:00","2020-04-21 18:00","취소","취소","연속"]
[293,"대전충남","아산","아산인주#1 T/L","[송전]154kV 아산-인주#1T/L 정밀점검","154kV 아산-인주#1T/L 아산ST ~ 인주ST(20기, 병가 제외) 정밀점검","2020-04-11 08:00","2020-04-11 18:00","2020-04-11 08:00","2020-04-11 18:00","연속"]
[294,"대전충남","아산","아산인주#2 T/L","[송전]154kV 아산-인주#2T/L 정밀점검","154kV 아산-인주#2T/L 아산ST ~ 인주ST(20기, 병가 제외) 정밀점검","2020-04-12 08:00","2020-04-12 18:00","2020-04-12 08:00","2020-04-12 18:00","연속"]
[295,"대전충남","아산","장재천안#2 T/L","[송전]154kV 장재-천안T/L 지장송전선로 이설공사(요청자시행)","ㅇ 요청자(동성산업개발) 직접시행 지장이설공사 ㅇ 공사구간 : 154kV 장재-천안T/L No.16~20 ㅇ 철탑 : 2기 교체 ㅇ 전력선 : HSTACIR/AW 410 x S x 2C (1.208km) ㅇ 철탑 2기, 가철탑 1기 설치철거 외 기타 부대공사 시행","2020-04-01 07:00","2020-04-15 18:00","2020-04-01 07:00","2020-04-15 18:00","연속"]
[296,"대전충남","아산","장재천안#1 T/L","[송전]154kV 장재-천안T/L 지장송전선로 이설공사(요청자시행)","ㅇ 요청자(동성산업개발) 직접시행 지장이설공사 ㅇ 공사구간 : 154kV 장재-천안T/L No.16~20 ㅇ 철탑 : 2기 교체 ㅇ 전력선 : HSTACIR/AW 410 x S x 2C (1.208km) ㅇ 철탑 2기, 가철탑 1기 설치철거 외 기타 부대공사 시행","2020-04-01 07:00","2020-04-15 18:00","2020-04-01 07:00","2020-04-15 18:00","연속"]
[297,"대전충남","직할","세종송강#1 T/L","[송전]국제과학비즈니스벨트 지장송전선로 지중화공사(요청자시행)","ㅇ 요청자(한국토지주택공사) 직접시행 지장이설 및 지중화공사 ㅇ 공사구간 : 154kV 세종-송강T/L No.16~17 ㅇ 철탑 : C/H 1기 설치, 가철탑 1기 ㅇ 전력선 : HSTACIR/AW 330 x S x 2C (1.041km) ㅇ CH 1기 설치, 가철탑 1기 설치철거 외 기타 부대공사 시행","2020-04-09 07:00","2020-04-26 18:00","취소","취소","연속"]
[298,"대전충남","직할","세종송강#2 T/L","[송전]국제과학비즈니스벨트 지장송전선로 지중화공사(요청자시행)","ㅇ 요청자(한국토지주택공사) 직접시행 지장이설 및 지중화공사 ㅇ 공사구간 : 154kV 세종-송강T/L No.16~17 ㅇ 철탑 : C/H 1기 설치, 가철탑 1기 ㅇ 전력선 : HSTACIR/AW 330 x S x 2C (1.041km) ㅇ CH 1기 설치, 가철탑 1기 설치철거 외 기타 부대공사 시행","2020-04-03 07:00","2020-04-08 18:00","취소","취소","연속"]
[299,"대전충남","직할","세종송강#1 T/L","[송전]국제과학비즈니스벨트 지장송전선로 지중화공사(요청자시행)","ㅇ 요청자(한국토지주택공사) 직접시행 지장이설 및 지중화공사 ㅇ 공사구간 : 154kV 세종-송강T/L No.16~17 ㅇ 철탑 : C/H 1기 설치, 가철탑 1기 ㅇ 전력선 : HSTACIR/AW 330 x S x 2C (1.041km) ㅇ CH 1기 설치, 가철탑 1기 설치철거 외 기타 부대공사 시행","2020-04-01 07:00","2020-04-02 18:00","취소","취소","연속"]
[300,"대전충남","대전","금산무주#1T/L","[송전]154kV 금산-무주T/L 정밀점검","[송전] 154kV 금산-무주#1T/L 정밀점검(금산S/T,No.1~2,10~81,무주S/T)","2020-04-16 08:00","2020-04-24 18:00","2020-04-16 08:00","2020-04-24 18:00","매일"]
[301,"전북","군산","군산동군산#2 T/L","군산동군산T/L 안전이격거리확보공사","- 철탑신설 2기 : 24, 26호 - 철탑철거 3기 : 24, 25, 26호 - 전선교체 : 20~26호","2020-04-06 07:00","2020-04-14 18:00","취소","취소","연속"]
[302,"전북","군산","군산이리#2 T/L","154㎸ 군산-이리T/L 안전이격거리확보공사","-가철탑신설 및 공중이동 : 2기(18,19호)","2020-04-30 09:00","2020-05-03 18:00","2020-04-30 09:00","2020-05-03 18:00","연속"]
[303,"전북","군산","군산이리#1 T/L","154㎸ 군산-이리T/L 안전이격거리확보공사","-가철탑신설 및 공중이동 : 2기(18,19호)","2020-04-27 09:00","2020-04-29 18:00","2020-04-27 09:00","2020-04-29 18:00","연속"]
[304,"전북","군산","군산서군산#2 T/L","154kV 군산-서군산T/L 정밀점검","기별점검 : No.1~70","2020-04-20 09:00","2020-04-24 18:00","취소","취소","매일"]
[305,"전북","군산","군산서군산#1 T/L","154kV 군산-서군산T/L 정밀점검","기별점검 : No.1~70","2020-04-06 09:00","2020-04-10 18:00","취소","취소","매일"]
[306,"전북","군산","군산동군산#1 T/L","군산동군산T/L 안전이격거리확보공사","- 철탑신설 2기 : 24, 26호 - 철탑철거 3기 : 24, 25, 26호 - 전선교체 : 20~26호","2020-04-15 07:00","2020-04-22 18:00","취소","취소","연속"]
[307,"전북","군산","내초군장#2 T/L","군산P/O 154kV이상 차단기 조작시험공사","군장S/S 154kV 내초-군장#2T/L 차단기 조작시험","2020-04-29 13:00","2020-04-29 16:00","취소","취소","연속"]
[308,"전북","군산","내초군장#1 T/L","군산P/O 154kV이상 차단기 조작시험공사","군장S/S 154kV 내초-군장#1T/L 차단기 조작시험","2020-04-29 09:30","2020-04-29 12:00","취소","취소","연속"]
[309,"전북","군산","군공내초#1 T/L","군산P/O 154kV이상 차단기 조작시험공사","내초S/S 154kV 군공-내초#1T/L CB 조작시험","2020-04-28 09:30","2020-04-28 12:00","취소","취소","연속"]
[310,"전북","군산","군공내초#2 T/L","군산P/O 154kV이상 차단기 조작시험공사","내초S/S 154kV 군공-내초#2T/L CB 조작시험","2020-04-28 13:00","2020-04-28 18:00","취소","취소","연속"]
[311,"전북","군산","서군산소룡#1 T/L","154kV 서군산-소룡T/L 정밀점검","기별점검 : No.1~16","2020-04-13 09:00","2020-04-13 18:00","취소","취소","연속"]
[312,"전북","군산","서군산소룡#2 T/L","154kV 서군산-소룡T/L 정밀점검","기별점검 : No.1~16","2020-04-14 09:00","2020-04-14 18:00","취소","취소","연속"]
[313,"전북","군산","이리전주#1 T/L","154kV 이리-전주T/L 일부지중화관련 철탑교체공사","- 철탑교체 4기 : 49, 50, 51, 52호 - 전선교체 : 47~50, 51~53호 - 가선로 구성 및 기타 부대공사 - C/H 50, 51호 옹벽 및 콘크리트 설치","2020-04-04 07:00","2020-04-06 18:00","취소","취소","연속"]
[314,"전북","군산","이리전주#2 T/L","154kV 이리-전주T/L 일부지중화관련 철탑교체공사","- 철탑교체 4기 : 49, 50, 51, 52호 - 전선교체 : 47~50, 51~53호 - 가선로 구성 및 기타 부대공사 - C/H 50, 51호 옹벽 및 콘크리트 설치","2020-04-07 07:00","2020-04-10 18:00","취소","취소","연속"]
[315,"전북","군산","이리전주#1 T/L","154kV 이리-전주T/L 일부지중화관련 철탑교체공사","- 철탑교체 4기 : 49, 50, 51, 52호 - 전선교체 : 47~50, 51~53호 - 가선로 구성 및 기타 부대공사 - C/H 50, 51호 옹벽 및 콘크리트 설치","2020-04-11 07:00","2020-04-11 18:00","2020-04-11 07:00","2020-04-11 18:00","연속"]
[316,"전북","김제","신김제남전주#1 T/L","154kV 남전주-임실T/L OPGW 증설공사","가공지선 철거후 OPGW 교체(38km) 및 항공구 정비","2020-04-20 09:00","2020-04-23 18:00","2020-04-20 09:00","2020-04-23 18:00","연속"]
[317,"전북","김제","신김제정공#1 T/L","신김제-동전주 및 정공T/L 정밀점검","No.1~11호","2020-04-09 09:00","2020-04-09 18:00","취소","취소","연속"]
[318,"전북","김제","정공정주#1 T/L","관내S/S 154kV 이상 차단기 보통점검 및 조작시험","관내S/S 154kV 이상 차단기 보통점검 및 조작시험","2020-04-13 09:00","2020-04-13 18:00","2020-04-13 09:00","2020-04-13 18:00","연속"]
[319,"전북","김제","정공정주#2 T/L","관내S/S 154kV 이상 차단기 보통점검 및 조작시험","관내S/S 154kV 이상 차단기 보통점검 및 조작시험","2020-04-14 09:00","2020-04-14 18:00","2020-04-14 09:00","2020-04-14 18:00","연속"]
[320,"전북","김제","신김제정공#2 T/L","신김제-동전주 및 정공T/L 정밀점검","No.1~11호","2020-04-02 09:00","2020-04-02 18:00","취소","취소","연속"]
[321,"전북","직할","신김제동전주#2 T/L","154kV 동전주-북전주 등 2개T/L 전력선 교체공사","전력선 교체 ○ 154kV 신김제-동전주#2T/L No.65~66 중,하단 4가닥","2020-04-10 07:30","2020-04-11 18:00","2020-04-11 07:00","2020-04-12 18:00","연속"]
[322,"전북","직할","신김제동전주#1 T/L","154kV 남전주-임실T/L OPGW 증설공사","가공지선 철거후 OPGW 교체(38km) 및 항공구 정비","2020-04-13 09:00","2020-04-14 18:00","2020-04-18 09:00","2020-04-19 18:00","매일"]
[323,"전북","직할","무주진안 T/L","무주S/S 혼용 운용 시스템반 제어케이블 이설공사","현장정보 처리반 제어케어블 공사","2020-04-03 09:00","2020-04-03 20:00","2020-04-03 09:00","2020-04-03 20:00","연속"]
[324,"전북","직할","무주용담수력 T/L","무주S/S 혼용 운용 시스템반 제어케이블 이설공사","현장정보 처리반 제어케어블 공사","2020-04-02 09:00","2020-04-02 20:00","2020-04-02 09:00","2020-04-02 20:00","연속"]
[325,"전북","직할","금산무주#2 T/L","무주S/S 혼용 운용 시스템반 제어케이블 이설공사","현장정보 처리반 제어케어블 공사","2020-04-03 09:00","2020-04-03 20:00","취소","취소","연속"]
[326,"전북","직할","금산무주#1 T/L","무주S/S 혼용 운용 시스템반 제어케이블 이설공사","현장정보 처리반 제어케어블 공사","2020-04-02 09:00","2020-04-02 20:00","취소","취소","연속"]
[327,"전북","직할","무주진안 T/L","[송전] 154kV 금산-무주T/L 정밀점검","[송전] 154kV 금산-무주#1T/L 정밀점검시 4회선구간 안전이격거리 확보","2020-04-20 08:00","2020-04-24 18:00","2020-04-20 08:00","2020-04-24 18:00","매일"]
[328,"전북","직할","팔봉봉동#1 T/L","관내 154kV 이상 차단기 점검공사","봉동SS 팔봉-봉동#1T/L 차단기 조작시험","2020-04-22 10:00","2020-04-22 14:00","취소","취소","연속"]
[329,"전북","직할","북전주봉동#2 T/L","관내 154kV 이상 차단기 점검공사","봉동SS 북전주-봉동#2T/L 차단기 조작시험 북전주SS 북전주-봉동#2T/L 차단기 보통점검","2020-04-24 10:00","2020-04-24 18:00","취소","취소","연속"]
[330,"전북","직할","북전주봉동#1 T/L","관내 154kV 이상 차단기 점검공사","봉동SS 북전주-봉동#1T/L 차단기 조작시험 북전주SS 북전주-봉동#1T/L 차단기 조작시험/ 전자변교체","2020-04-23 10:00","2020-04-23 18:00","취소","취소","연속"]
[331,"전북","직할","팔봉봉동#2 T/L","관내 154kV 이상 차단기 점검공사","봉동SS 팔봉-봉동#2T/L 차단기 조작시험","2020-04-22 14:00","2020-04-22 18:00","취소","취소","연속"]
[332,"전북","직할","북전주진안 T/L","154kV 동전주-북전주 등 2개T/L 전력선 교체공사","4회선 병가구간 안전작업 확보","2020-04-04 07:30","2020-04-04 18:00","2020-04-04 07:30","2020-04-04 18:00","연속"]
[333,"전북","직할","이리전주#1 T/L","154kV 탄소분기 지중T/L 건설공사","- 기설 이리-전주#1T/L 케이블 절단 후 이리-탄소#1T/L 접속","2020-04-17 10:00","2020-05-22 18:00","2020-04-17 10:00","2020-05-22 18:00","연속"]
[334,"광주전남","순천","승주서순천 T/L","20년 상반기 170kV GIS 정밀점검공사","승주S/S 승주-서순천T/L GIS 정밀점검 공사","2020-04-02 09:00","2020-04-03 18:00","2020-04-02 09:00","2020-04-03 18:00","연속"]
[335,"광주전남","순천","용성여수산단#1 T/L","154kV 용성S/S LG화학 신규수용공사","170kV GIS SEC DS 전단 모선부분 가압","2020-04-02 15:00","2020-04-03 15:00","2020-04-02 15:00","2020-04-03 15:00","연속"]
[336,"광주전남","순천","계림승주#1 T/L","20년 상반기 170kV GIS 정밀점검공사","승주S/S 계림-승주#1T/L GIS 정밀점검 공사","2020-04-06 09:00","2020-04-07 18:00","2020-04-06 09:00","2020-04-07 18:00","연속"]
[337,"광주전남","순천","여수TP용성#2 T/L","일진제 170kV GIS 유사고장 조치공사 및 정밀점검","용성S/S 여수TP-용성#2T/L GIS 유사고장 조치 및 정밀점검","2020-04-06 09:00","2020-04-09 18:00","2020-04-06 09:00","2020-04-10 18:00","연속"]
[338,"광주전남","광주","계림충장#2 T/L","20년 광주변전총액공사(계림충장#2T/L)","계림충장#2T/L 충장 측 GIS 보통점검, 계림 측 장기미동작 CB점검","2020-04-08 09:00","2020-04-08 18:00","2020-04-13 09:00","2020-04-13 18:00","연속"]
[339,"광주전남","순천","계림승주#2 T/L","20년 상반기 170kV GIS 정밀점검공사","승주S/S 계림-승주#2T/L GIS 정밀점검 공사","2020-04-08 09:00","2020-04-09 18:00","2020-04-08 09:00","2020-04-09 18:00","연속"]
[340,"광주전남","직할","왕곡나주#1 T/L","왕곡 변전기자재 실증시험장 신축공사","○실증시험장 외부패널 설치","2020-04-09 09:00","2020-04-17 18:00","취소","취소","연속"]
[341,"광주전남","직할","평동왕곡#1 T/L","왕곡 변전기자재 실증시험장 신축공사","○실증시험장 외부패널 설치","2020-04-09 09:00","2020-04-17 18:00","취소","취소","연속"]
[342,"광주전남","순천","승주주암HP T/L","20년 상반기 170kV GIS 정밀점검공사","승주S/S 승주-주암HP T/L GIS 정밀점검 공사","2020-04-13 09:00","2020-04-14 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[343,"광주전남","순천","여천여수#1 T/L","20~21년 순천전력지사 변전총액공사(LA 하자점검)","여수S/S 여천-여수#1T/L LA(A,B,C) 하자점검 및 GIS 타임측정 여천S/S 여천-여수#1T/L GIS 타임측정","2020-04-16 09:00","2020-04-16 18:00","2020-04-16 09:00","2020-04-16 18:00","연속"]
[344,"광주전남","순천","율촌민자#2 T/L","20년 상반기 170kV GIS 정밀점검 공사","율촌S/S 율촌-민자#2T/L GIS 정밀점검(4.16~4.17)","2020-04-16 09:00","2020-04-19 18:00","2020-04-16 09:00","2020-04-19 18:00","연속"]
[345,"광주전남","광주","담양일곡#1 T/L","154kV 담양-일곡T/L 190-192호 지장송전선로 지중화공사","154kV 담양-일곡 No.188~193 본선로 구성(요청자 시행공사) - 기설 NO.188~신설C/H No.1간 - C/H No.2 ~기설 No.193간 - 전선교체 : ACSR 240㎟xS, 0.88km","2020-04-17 08:00","2020-04-19 18:00","2020-04-25 08:00","2020-04-27 18:00","연속"]
[346,"광주전남","순천","여천여수#2 T/L","20~21년 순천전력지사 변전총액공사(LA 하자점검)","여수S/S 여천-여수#2T/L LA(A,B,C) 하자점검 및 GIS 타임측정 여천S/S 여천-여수#2T/L GIS 타임측정","2020-04-17 09:00","2020-04-17 18:00","2020-04-17 09:00","2020-04-17 18:00","연속"]
[347,"광주전남","광주","담양일곡#2 T/L","154kV 담양-일곡T/L 190-192호 지장송전선로 지중화공사","154kV 담양-일곡 No.188~193 본선로 구성(요청자 시행공사) - 기설 NO.188~신설C/H No.1간 - C/H No.2 ~기설 No.193간 - 전선교체 : ACSR 240㎟xS, 0.88km","2020-04-20 08:00","2020-04-22 18:00","2020-04-28 08:00","2020-04-30 18:00","연속"]
[348,"광주전남","광주","신광주계림#1 T/L","신광주-계림T/L OPGW 증설공사","신광주-계림T/L 광코어 부족 해소를 위한 OPGW 교체(24C→48C)","2020-04-20 08:00","2020-04-24 18:00","취소","취소","연속"]
[349,"광주전남","목포","나주엄다#1 T/L","'20년 목포전력지사 변전정비회사 총액공사","엄다S/S 나주-엄다#1T/L 차단기 조작시험","2020-04-20 09:00","2020-04-20 14:00","2020-04-20 09:00","2020-04-20 14:00","연속"]
[350,"광주전남","순천","여수TP용성#1 T/L","일진제 170kV GIS 유사고장 조치공사 및 정밀점검","용성S/S 여수TP-용성#1T/L GIS 유사고장 조치 및 정밀점검","2020-04-20 09:00","2020-04-23 18:00","2020-04-20 09:00","2020-04-24 18:00","연속"]
[351,"광주전남","순천","율촌민자#1 T/L","20년 상반기 170kV GIS 정밀점검 공사","율촌S/S 율촌-민자#1T/L GIS 정밀점검(4.20~4.21)","2020-04-20 09:00","2020-04-23 18:00","2020-04-20 09:00","2020-04-23 18:00","연속"]
[352,"광주전남","목포","나주엄다#2 T/L","'20년 목포전력지사 변전정비회사 총액공사","엄다S/S 나주-엄다#2T/L 차단기 조작시험","2020-04-20 14:00","2020-04-20 18:00","2020-04-20 14:00","2020-04-20 18:00","연속"]
[353,"광주전남","목포","안좌신안그린 T/L CB","`20년 목포전력지사 변전정비회사 총액공사","신안그린T/L 차단기 조작시험","2020-04-21 10:00","2020-04-21 14:00","2020-04-21 10:00","2020-04-21 14:00","연속"]
[354,"광주전남","광주","계림승주#1 T/L","신광주-계림T/L OPGW 증설공사","신광주-계림T/L 광코어 부족 해소를 위한 OPGW 교체(24C→48C)","2020-04-23 08:00","2020-04-23 18:00","취소","취소","연속"]
[355,"광주전남","광주","신광주계림#2 T/L","신광주-계림T/L OPGW 증설공사","신광주-계림T/L 광코어 부족 해소를 위한 OPGW 교체(24C→48C)","2020-04-23 08:00","2020-04-23 18:00","취소","취소","연속"]
[356,"광주전남","순천","용성여수산단#1 T/L","일진제 170kV GIS 유사고장 조치공사 및 정밀점검","유사고장 조치공사 후 무부하 가압","2020-04-23 09:00","2020-04-24 18:00","2020-04-23 09:00","2020-04-24 18:00","연속"]
[357,"광주전남","순천","순천율촌#2 T/L","율촌S/S 인출철구 보강공사","인출철구 보강공사(안전이격거리 확보)","2020-04-23 09:00","2020-04-23 18:00","2020-04-23 09:00","2020-04-23 18:00","연속"]
[358,"광주전남","순천","광양순천#2 T/L","20-21년 순천전력지사 송전정비회사 총액공사","154kV 광양-순천#2T/L 장기사용 성능진단 애자발췌 - 애자교체 3기(163,164,167)","2020-04-27 08:00","2020-04-28 18:00","2020-04-27 08:00","2020-04-28 18:00","매일"]
[359,"광주전남","순천","광양순천#1 T/L","20-21년 순천전력지사 송전정비회사 총액공사","154kV 광양-순천#1T/L 국산애자교체 - 애자교체 2기(6,167호)","2020-04-29 08:00","2020-04-29 18:00","2020-04-29 08:00","2020-04-29 18:00","연속"]
[360,"광주전남","광주","신광주일곡#1 T/L"," 신광주,일곡S/S 신광주-일곡#1T/L 송전선로 보호반 교체","신광주S/S 신광주-일곡#1T/L GIS 하자점검 신광주S/S 신광주-일곡#1T/L LA C상 절연 볼트 불량 관련 점검","2020-04-01 09:00","2020-04-03 18:00","2020-04-01 09:00","2020-04-03 18:00","연속"]
[361,"광주전남","강진","남창해남CS#1 T/L"," 남창S/S 154kV 남창-해남C/S #1T/L GIS 조작시험","조작시험 및 개폐타임 측정","2020-04-01 10:00","2020-04-01 14:00","2020-04-01 10:00","2020-04-01 14:00","연속"]
[362,"광주전남","강진","남창해남CS#2 T/L"," 남창S/S 154kV 남창-해남C/S #2T/L GIS 조작시험","조작시험 및 개폐타임 측정","2020-04-01 14:00","2020-04-01 18:00","2020-04-01 14:00","2020-04-01 18:00","연속"]
[363,"광주전남","강진","강진남창#1 T/L"," 남창S/S 154kV 강진-남창#1T/L GIS 조작시험","조작시험 및 개폐타임 측정","2020-04-02 10:00","2020-04-02 14:00","2020-04-02 10:00","2020-04-02 14:00","연속"]
[364,"광주전남","강진","강진남창#2 T/L"," 남창S/S 154kV 강진-남창#2T/L GIS 조작시험","조작시험 및 개폐타임 측정","2020-04-02 14:00","2020-04-02 18:00","2020-04-02 14:00","2020-04-02 18:00","연속"]
[365,"광주전남","광주","신광주일곡#2 T/L"," 신광주,일곡S/S 신광주-일곡#2T/L 송전선로 보호반 교체","신광주S/S 신광주-일곡#2T/L GIS 하자점검","2020-04-06 09:00","2020-04-08 18:00","2020-04-06 08:00","2020-04-08 18:00","연속"]
[366,"광주전남","광주","계림충장#1 T/L"," 20년 광주변전총액공사(계림충장#1T/L)","계림충장#1T/L 충장 측 GIS 보통점검, 계림 측 장기미동작 CB점검","2020-04-09 09:00","2020-04-09 18:00","2020-04-09 09:00","2020-04-09 18:00","연속"]
[367,"광주전남","광주","일곡비아#2 T/L"," 2020년 광주전력지사 170kV GIS 정밀점검공사","2020년 광주전력지사 170kV GIS 정밀점검공사","2020-04-13 09:00","2020-04-14 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[368,"광주전남","광주","신화순나주#2 T/L","  20년 광주변전총액공사(신화순나주2T/L LA하자점검)","신화순S/S 신화순-나주#2T/L LA하자점검","2020-04-21 09:00","2020-04-21 18:00","2020-04-21 09:00","2020-04-21 18:00","연속"]
[369,"광주전남","광주","충장농성#1 T/L"," 20년 광주변전총액공사(충장농성#1T/L)","충장농성#1T/L 충장 측 GIS 보통점검","2020-04-22 09:30","2020-04-22 14:00","2020-04-22 09:30","2020-04-22 14:00","연속"]
[370,"광주전남","광주","충장농성#2 T/L"," 20년 광주변전총액공사(충장농성#12/L)","충장농성#2T/L 충장 측 GIS 보통점검","2020-04-22 14:00","2020-04-22 18:00","2020-04-22 14:00","2020-04-22 18:00","연속"]
[371,"광주전남","광주","계림S/S 154kV #60-#65 BUS TIE GIS"," 20년 광주변전총액공사(계림 6100)","계림S/S 6100 BusTie 장기미동작 CB점검","2020-04-23 09:30","2020-04-23 11:00","2020-04-23 09:30","2020-04-23 11:00","연속"]
[372,"광주전남","광주","계림S/S 154kV #61-#66 BUS TIE GIS"," 20년 광주변전총액공사(계림 6200)","계림S/S 6100 BusTie 장기미동작 CB점검","2020-04-23 11:00","2020-04-23 13:30","2020-04-23 11:00","2020-04-23 13:30","연속"]
[373,"광주전남","광주","계림S/S 154kV #60-61 SEC GIS"," 20년 광주변전총액공사(계림 6061)","계림S/S 6100 BusTie 장기미동작 CB점검","2020-04-23 13:30","2020-04-23 15:30","2020-04-23 13:30","2020-04-23 15:30","연속"]
[374,"광주전남","광주","계림S/S 154kV #65-66 SEC GIS"," 20년 광주변전총액공사(계림 6566)","계림S/S 6100 BusTie 장기미동작 CB점검","2020-04-23 15:30","2020-04-23 18:00","2020-04-23 15:30","2020-04-23 18:00","연속"]
[375,"광주전남","강진","진도CS서제주#1 T/L CB"," `20~`21년도 #2HVDC 변환설비 위탁정비공사","#2HVDC 변환설비 연차점검(#1Pole)","2020-04-25 09:00","2020-05-05 18:00","2020-04-25 09:00","2020-05-05 18:00","연속"]
[376,"광주전남","광주","정공담양 T/L"," 20년 광주변전총액공사(정공담양T/L)","담양S/S 정공담양T/L 장기미동작 CB점검, CVT 초기점검","2020-04-27 09:30","2020-04-27 13:30","취소","취소","연속"]
[377,"광주전남","광주","담양김제 T/L"," 20년 광주변전총액공사(담양김제T/L)","담양S/S 정공담양T/L 장기미동작 CB점검, CVT 초기점검","2020-04-27 13:30","2020-04-27 18:00","취소","취소","연속"]
[378,"광주전남","광주","신광주장성#1 T/L","  20년 광주변전총액공사(신광주장성1T/L LA하자점검)","장성S/S 신광주장성1T/L LA하자점검","2020-04-28 09:00","2020-04-28 13:00","2020-04-28 09:00","2020-04-28 13:00","연속"]
[379,"광주전남","광주","신광주장성#2 T/L"," 20년 광주변전총액공사(신광주장성 2T/L)","장성S/S 신광주장성2T/L 장기미동작 CB점검, LA 하자점검","2020-04-28 13:00","2020-04-28 18:00","2020-04-28 13:00","2020-04-28 18:00","연속"]
[380,"광주전남","강진","진도CS서제주#2 T/L CB"," `20~`21년도 #2HVDC 변환설비 위탁정비공사","#2HVDC 변환설비 연차점검(#2Pole)","2020-04-30 09:00","2020-05-10 18:00","2020-04-30 09:00","2020-05-10 18:00","연속"]
[381,"대구","경산","청도밀양#1 T/L","20~21년 달성 송전정비회사 총액공사","항공장애표시구 설치공사(안전 이격)","2020-04-11 14:00","2020-04-11 18:00","2020-04-11 14:00","2020-04-11 18:00","연속"]
[382,"대구","경산","청도밀양#2 T/L","20~21년 달성 송전정비회사 총액공사","항공장애표시구 설치공사(안전 이격)","2020-04-11 07:30","2020-04-11 14:00","2020-04-11 07:30","2020-04-11 14:00","연속"]
[383,"대구","달성","고령쌍림#1 T/L","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-26 08:00","2020-04-30 18:00","취소","취소","연속"]
[384,"대구","달성","고령S/S 154kV #65 BUS","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-24 18:00","2020-04-25 18:00","취소","취소","연속"]
[385,"대구","달성","고령S/S 154kV #66 BUS","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-24 17:00","2020-04-24 18:00","취소","취소","연속"]
[386,"대구","달성","고령다산#1 T/L","고령S/S 154kV #61-#66 BUS-TIE 정밀점검","고령S/S 154kV #61-#66 BUS-TIE 정밀점검","2020-04-24 14:00","2020-04-25 18:00","2020-04-24 14:00","2020-04-25 18:00","매일"]
[387,"대구","달성","고령S/S 154kV #66 BUS","고령S/S 154kV #61-#66 BUS-TIE 정밀점검","고령S/S 154kV #61-#66 BUS-TIE 정밀점검","2020-04-24 14:00","2020-04-25 18:00","2020-04-24 14:00","2020-04-25 18:00","연속"]
[388,"대구","달성","고령S/S 154kV #61-#66 BUS TIE CB","고령S/S 154kV #61-#66 BUS-TIE 정밀점검","고령S/S 154kV #61-#66 BUS-TIE 정밀점검","2020-04-23 09:00","2020-04-25 18:00","2020-04-23 09:00","2020-04-25 18:00","연속"]
[389,"대구","달성","고령S/S 154kV #61 BUS","고령S/S 154kV #61-#66 BUS-TIE 정밀점검","고령S/S 154kV #61-#66 BUS-TIE 정밀점검","2020-04-23 09:00","2020-04-24 14:00","2020-04-23 09:00","2020-04-24 14:00","연속"]
[390,"대구","달성","고령다산#2 T/L","고령S/S 154kV #66-#67 BUS SEC 정밀점검","고령S/S 154kV #66-#67 BUS SEC 정밀점검[TEST선로]","2020-04-21 14:00","2020-04-22 18:00","2020-04-21 14:00","2020-04-22 18:00","매일"]
[391,"대구","달성","고령다산#2 T/L","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-21 08:00","2020-04-25 18:00","취소","취소","연속"]
[392,"대구","달성","고령쌍림#2 T/L","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-21 08:00","2020-04-26 18:00","취소","취소","연속"]
[393,"대구","달성","고령다산#1 T/L","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-20 14:00","2020-04-20 17:00","취소","취소","연속"]
[394,"대구","달성","고령쌍림#2 T/L","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-20 11:00","2020-04-20 14:00","취소","취소","연속"]
[395,"대구","달성","고령쌍림#1 T/L","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-20 09:00","2020-04-20 11:00","취소","취소","연속"]
[396,"대구","달성","고령S/S 154kV #66 BUS","고령S/S 154kV #66-#67 BUS SEC 정밀점검","고령S/S 154kV #61-#62 BUS SEC 정밀점검","2020-04-20 09:00","2020-04-21 14:00","2020-04-20 09:00","2020-04-21 14:00","연속"]
[397,"대구","달성","고령다산#1 T/L","고령S/S 154kV #61-#62 BUS SEC 정밀점검","고령S/S 154kV #61-#62 BUS SEC 정밀점검[TEST선로]","2020-04-17 14:00","2020-04-18 18:00","2020-04-17 14:00","2020-04-18 18:00","연속"]
[398,"대구","달성","고령S/S 154kV #61 BUS","고령S/S 154kV #61-#62 BUS SEC 정밀점검","고령S/S 154kV #61-#62 BUS SEC 정밀점검","2020-04-16 09:00","2020-04-17 14:00","2020-04-16 09:00","2020-04-17 14:00","연속"]
[399,"대구","달성","고령논공#1 T/L","고령S/S 154kV #3SC 정밀점검(DS포함)[TEST선로]","고령S/S 154kV #3SC 정밀점검(DS포함)[TEST선로]","2020-04-10 14:00","2020-04-11 18:00","2020-04-10 14:00","2020-04-11 18:00","연속"]
[400,"대구","달성","고령다산#1 T/L","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-26 08:00","2020-04-30 18:00","취소","취소","연속"]
[401,"대구","달성","고령S/S 154kV #61 BUS","고령변전소 154kV 송전선로 인출변경","고령변전소 154kV 송전선로 인출변경","2020-04-29 17:00","2020-04-29 18:00","취소","취소","연속"]
[402,"대구","달성","고령논공#1 T/L","고령S/S #62-#67 BUS TIE 정밀점검","고령S/S #62-#67 BUS TIE 정밀점검(TEST선로)","2020-04-28 14:00","2020-04-29 18:00","2020-04-28 14:00","2020-04-29 18:00","매일"]
[403,"대구","달성","다산강창#1 T/L","다산S/S 154kV BUS-TIE 정밀점검","다산S/S 154kV BUS-TIE 정밀점검(TEST선로)","2020-04-07 14:00","2020-04-08 18:00","2020-04-07 14:00","2020-04-08 18:00","연속"]
[404,"대구","달성","대구청도#1 T/L","20~21년 달성 송전정비회사 총액공사","항공장애표시구 설치공사(안전 이격)","2020-04-11 07:30","2020-04-11 14:00","2020-04-11 07:30","2020-04-11 14:00","연속"]
[405,"대구","달성","대구청도#2 T/L","20~21년 달성 송전정비회사 총액공사","항공장애표시구 설치공사(안전 이격)","2020-04-11 14:00","2020-04-11 18:00","2020-04-11 14:00","2020-04-11 18:00","연속"]
[406,"대구","달성","쌍림합천#2 T/L","쌍림S/S 쌍림-합천#2T/L 정밀점검(DS포함)","쌍림S/S 쌍림-합천#2T/L 정밀점검(DS포함)","2020-04-02 09:00","2020-04-04 18:00","취소","취소","연속"]
[407,"대구","칠곡","칠곡인동#1 T/L","선산분기T/L 전력선교체공사 안전확보","선산분기T/L 전력선교체공사 안전확보","2020-04-20 08:00","2020-04-24 18:00","2020-04-22 08:00","2020-04-25 18:00","매일"]
[408,"대구","칠곡","칠곡인동#2 T/L","선산분기T/L 전력선교체공사 안전확보","선산분기T/L 전력선교체공사 안전확보","2020-04-20 08:00","2020-04-24 18:00","2020-04-22 08:00","2020-04-25 18:00","매일"]
[409,"대구","포항","신영일천북#1 T/L","345kV 신포항-북대구T/L 전력선교체공사(안전확보)","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-20 07:00","2020-04-26 18:00","2020-04-27 07:00","2020-05-03 18:00","매일"]
[410,"대구","포항","신영일천북#2 T/L","345kV 신포항-북대구T/L 전력선교체공사(안전확보)","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-20 07:00","2020-04-26 18:00","2020-04-27 07:00","2020-05-03 18:00","매일"]
[411,"대구","포항","신영일천북#1 T/L","345kV 신포항-북대구T/L 전력선교체공사(안전확보)","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-01 07:00","2020-04-07 18:00","취소","취소","매일"]
[412,"대구","포항","신영일천북#2 T/L","345kV 신포항-북대구T/L 전력선교체공사(안전확보)","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-01 07:00","2020-04-07 18:00","취소","취소","매일"]
[413,"대구","포항","영일입실 T/L","345kV 신포항-북대구T/L 전력선교체공사(안전확보)","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-10 07:00","2020-04-16 18:00","취소","취소","매일"]
[414,"대구","포항","영일상정 T/L","345kV 신포항-북대구T/L 전력선교체공사(안전확보)","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-10 07:00","2020-04-16 18:00","취소","취소","매일"]
[415,"대구","포항","영일상정 T/L","345kV 신포항-북대구T/L 전력선교체공사(안전확보)","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-23 07:00","2020-04-29 18:00","2020-04-20 07:00","2020-04-26 18:00","매일"]
[416,"대구","포항","영일입실 T/L","345kV 신포항-북대구T/L 전력선교체공사(안전확보)","345kV 신포항-북대구T/L 전력선교체공사 공사구간 : 345kV 신포항-북대구T/L No.202~205, 208~219, 265~272 전력선교체 : ACSR 480㎟*4B*2C, 14.645C_km 가공지선교체 : ACSR 120㎟ 7.623C_km","2020-04-23 07:00","2020-04-29 18:00","2020-04-20 07:00","2020-04-26 18:00","매일"]
[417,"대구","경산","하양반야월#2 T/L","154kV 신서분기 지중T/L 건설공사","신서E/C~154kV 하양-반야월T/L 분기맨홀(2파이 분기) 154kV XLPE1200*2C(D) 0.5km, 154kV XLPE2500*2C 0.5km","2020-04-13 09:00","2020-05-04 18:00","2020-04-13 09:00","2020-05-04 18:00","연속"]
[418,"경북","구미","동상주점촌#2 T/L","154kV 동상주-점촌T/L 지장이설공사","- 154kV 동상주-점촌T/L No.7-9호 전선 공중이동","2020-04-23 08:00","2020-04-25 18:00","2020-04-29 08:00","2020-05-01 18:00","연속"]
[419,"경북","구미","동상주점촌#1 T/L","154kV 동상주-점촌T/L 지장이설공사","- 154kV 동상주-점촌T/L No.7-9호 전선 공중이동","2020-04-20 08:00","2020-04-22 18:00","2020-04-26 08:00","2020-04-28 18:00","연속"]
[420,"경북","영주","신영주안동#1 T/L","20-21영주전력송전총액(154kV 신영주-안동T/L 전선교체 공사)","No.38-43, 44-52 전선접속개소 제거","2020-04-06 07:00","2020-04-14 18:00","2020-04-06 07:00","2020-04-14 18:00","연속"]
[421,"경북","영주","신영주예천#1 T/L","154kV 신영주-예천T/L 전선접속개소 전선교체공사","154kV 신영주-예천T/L 전선접속개소 전선교체공사(17-28호, 36호-44호)","2020-04-03 09:00","2020-04-14 18:00","2020-04-03 09:00","2020-04-14 18:00","연속"]
[422,"경북","영주","신영주안동#2 T/L","20-21영주전력송전총액(154kV 신영주-안동T/L 전선교체 공사)","No.38-43, 44-52 전선접속개소 제거","2020-04-16 07:00","2020-04-24 18:00","2020-04-16 07:00","2020-04-24 18:00","연속"]
[423,"경북","영주","신영주예천#2 T/L","154kV 신영주-예천T/L 전선접속개소 전선교체공사","154kV 신영주-예천T/L 전선접속개소 전선교체공사(17-28호, 36호-44호)","2020-04-16 09:00","2020-04-27 18:00","2020-04-16 09:00","2020-04-27 18:00","연속"]
[424,"경북","직할","안동S/S 154kV 안동-풍산T/L GIS","20~21년 경북본부 직할 변전정비회사 총액공사","GIS 조작시험","2020-04-21 09:00","2020-04-21 18:00","취소","취소","연속"]
[425,"경북","직할","현종산풍력평해#2 T/L","154kV 평해S/S 옥외철구설비 현대화 공사","○현종산풍력-평해#2T/L GIS로 전환 - 인출모선 조정, 보호반 이설, 전력선 교체, OPGW 이설, 준공시험","2020-04-21 09:00","2020-04-29 18:00","2020-04-21 09:00","2020-04-29 18:00","연속"]
[426,"부산울산","북부산","물금삼랑진PP#2 T/L","2020년도 북부산 가공위탁공사","154kV 물금-삼랑진#2T/L 송전선로 정밀점검(1~58호, 58기)","2020-04-07 09:00","2020-04-11 18:00","2020-04-07 10:00","2020-04-07 18:00","매일"]
[427,"부산울산","북부산","호포물금 T/L","2020년도 북부산 가공위탁공사","154kV 북부산-물금T/L(호포-물금T/L) 송전선로 정밀점검(1~46호, 45기)","2020-04-18 09:00","2020-04-19 18:00","2020-04-26 10:00","2020-04-26 18:00","매일"]
[428,"부산울산","북부산","북부산물금 T/L","20-21년 북부산전력지사 가공송전 협력회사 총액공사","154kV 북부산호포T/L 작업 안전이격휴전","2020-04-16 08:00","2020-04-19 13:00","2020-04-16 08:00","2020-04-19 13:00","연속"]
[429,"부산울산","북부산","물금삼랑진PP#2 T/L","20-21년 북부산전력지사 가공송전 협력회사 총액공사","154kV 물금삼랑진#1T/L 작업 안전이격휴전","2020-04-06 13:00","2020-04-06 18:00","2020-04-06 13:00","2020-04-06 18:00","연속"]
[430,"부산울산","북부산","물금삼랑진PP#1 T/L","2020년 북부산 가공송전선로 순시점검 위탁공사","물금삼랑진#2T/L 정밀점검 안전이격휴전","2020-04-07 09:00","2020-04-11 18:00","취소","취소","매일"]
[431,"부산울산","북부산","물금삼랑진PP#1 T/L","20-21년 북부산전력지사 가공송전 협력회사 총액공사","154kV 물금삼랑진#1T/L 회전스페이서 교체작업","2020-04-06 13:00","2020-04-06 18:00","2020-04-06 13:00","2020-04-06 18:00","연속"]
[432,"부산울산","북부산","북부산S/S 154kV #66 BUS","북부산S/S 154kV 송전선로 인출Bay 조정 공사","북부산S/S 154kV 송전선로 인출Bay 조정 공사 1차 (신6D2 DS 설치)","2020-04-06 08:00","2020-04-11 16:00","2020-04-06 08:00","2020-04-11 16:00","연속"]
[433,"부산울산","북부산","북부산S/S 154kV #61 BUS","북부산S/S 154kV 송전선로 인출Bay 조정 공사","북부산S/S 154kV 송전선로 인출Bay 조정 공사 1차 (신6D1 DS 시험가압 2H)","2020-04-11 16:00","2020-04-11 18:00","2020-04-11 16:00","2020-04-11 18:00","연속"]
[434,"부산울산","북부산","북부산물금 T/L","2020년도 북부산 가공위탁공사","154kV 북부산-물금T/L 송전선로 정밀점검(1~46호, 45기)","2020-04-13 09:00","2020-04-15 18:00","2020-04-27 08:00","2020-04-27 18:00","매일"]
[435,"부산울산","북부산","북부산호포 T/L","2020년도 북부산 가공위탁공사","154kV 북부산-물금T/L(북부산-호포T/L) 송전선로 정밀점검(1~46호, 45기)","2020-04-25 09:00","2020-04-26 18:00","2020-04-27 08:00","2020-04-27 18:00","매일"]
[436,"부산울산","북부산","서창산막#2 T/L","154kV 서창-산막T/L 13호 지장철탑 이설공사","- 4/30 ~ 5/1 : #2T/L 본선로 구성, 13호 철탑 조립","2020-04-30 07:00","2020-05-01 18:00","2020-04-30 07:00","2020-05-01 18:00","연속"]
[437,"부산울산","북부산","언양산막#1 T/L","20년도 가공송전 순시점검 위탁공사(정밀점검)","안전거리확보(154kV 반천-언양#2T/L 휴전관련)","2020-04-24 08:30","2020-04-24 18:00","2020-04-24 08:30","2020-04-24 18:00","연속"]
[438,"부산울산","북부산","서창산막#1 T/L","154kV 서창-산막T/L 13호 지장철탑 이설공사","- 4/25 ~ 26 : #1T/L 가선로 구성","2020-04-25 07:00","2020-04-26 18:00","2020-04-26 07:00","2020-04-26 18:00","연속"]
[439,"부산울산","북부산","언양산막#2 T/L","20년도 가공송전 순시점검 위탁공사(정밀점검)","안전거리확보(154kV 반천-언양#1T/L 휴전관련)","2020-04-20 08:30","2020-04-20 18:00","2020-04-20 08:30","2020-04-20 18:00","연속"]
[440,"부산울산","북부산","물금삼랑진PP#2 T/L","154kV 삼랑진양수 스위치야드 현대화 사업","○ 삼랑진양수 현대화공사 관련 발전선로 #1,2M.Tr Bay 계통병입 관련 시험가압 및 본가압","2020-04-29 09:00","2020-04-30 18:00","2020-04-29 09:00","2020-04-30 18:00","연속"]
[441,"부산울산","북부산","양산E/C 154kV #60-#61 SEC CB","'20-21 북부산전력지사 변전정비회사 총액공사","양산S/S 154kV BUS-SECTION 60-61 GIS 하자점검","2020-04-08 10:00","2020-04-08 18:00","2020-04-08 10:00","2020-04-08 18:00","연속"]
[442,"부산울산","북부산","양산E/C 154kV #65-#66 SEC CB","'20-21 북부산전력지사 변전정비회사 총액공사","양산S/S 154kV BUS-SECTION 65-66 GIS 하자점검","2020-04-09 10:00","2020-04-09 18:00","2020-04-09 10:00","2020-04-09 18:00","연속"]
[443,"부산울산","북부산","삼계어방#2 T/L","'20-21 북부산전력지사 변전정비회사 총액공사","삼계S/S 154kV 삼계-어방#2T/L GIS 하자점검","2020-04-05 10:00","2020-04-05 18:00","2020-04-05 10:00","2020-04-05 18:00","연속"]
[444,"부산울산","서부산","녹공S/S 154kV 녹공-마천#1T/L GIS","녹공S/S 154kV 녹공-마천#1T/L GIS 보통점검","녹공S/S 154kV 녹공-마천#1T/L GIS 보통점검","2020-04-27 10:00","2020-04-27 18:00","2020-04-27 10:00","2020-04-27 18:00","연속"]
[445,"부산울산","서부산","녹공S/S 154kV 녹공-마천#2T/L GIS","녹공S/S 154kV 녹공-마천#2T/L GIS 보통점검","녹공S/S 154kV 녹공-마천#2T/L GIS 보통점검","2020-04-28 10:00","2020-04-28 18:00","2020-04-28 10:00","2020-04-28 18:00","연속"]
[446,"부산울산","서부산","서부산다대#1 T/L","154kV 서부산-다대T/L 지장이설 및 선종교체공사","선로명 : 154kV 서부산-다대#1T/L 구 간 : J/B#2 ~ J/B#5 (1.01km) 작업내용 : 을숙도대교-장림고개간 지하차도건설공사에 따른 지장이설 및 케이블 선종교체","2020-04-01 09:00","2020-06-01 18:00","2020-04-01 09:00","2020-06-01 18:00","연속"]
[447,"부산울산","서부산","서부산S/S 154kV #60-#65 BUS TIE GIS","서부산S/S 154kV #6100 TIE GIS 보통점검","서부산S/S 154kV #6100 TIE GIS 보통점검","2020-04-07 10:00","2020-04-07 18:00","2020-04-07 10:00","2020-04-07 18:00","연속"]
[448,"부산울산","서부산","서부산S/S 154kV #61-#66 BUS TIE GIS","서부산S/S 154kV #6200 TIE GIS 보통점검","서부산S/S 154kV #6200 TIE GIS 보통점검","2020-04-08 10:00","2020-04-08 18:00","2020-04-08 10:00","2020-04-08 18:00","연속"]
[449,"부산울산","서부산","서부산S/S 154kV #60-#61 SEC GIS","서부산S/S 154kV #60-61 SEC GIS 차단기 동작시험","서부산S/S 154kV #60-61 SEC GIS 차단기 동작시험","2020-04-09 10:00","2020-04-09 18:00","2020-04-09 10:00","2020-04-09 18:00","연속"]
[450,"부산울산","서부산","서부산S/S 154kV 서부산-엄궁#1T/L GIS","서부산S/S 154kV 서부산-엄궁#1T/L GIS 보통점검","서부산S/S 154kV 서부산-엄궁#1T/L GIS 보통점검","2020-04-17 10:00","2020-04-17 18:00","2020-04-17 10:00","2020-04-17 18:00","연속"]
[451,"부산울산","서부산","서부산S/S 154kV #65-#66 SEC GIS","서부산S/S 154kV #65-66 SEC GIS 차단기 동작시험","서부산S/S 154kV #65-66 SEC GIS 차단기 동작시험","2020-04-10 10:00","2020-04-10 18:00","2020-04-10 10:00","2020-04-10 18:00","연속"]
[452,"부산울산","서부산","신김해지사#2 T/L","보호IED ~ SCADA 원격소장치 연계시스템 시설공사","선로명 : 154kV 지사-미음#1 T/L 작업내용 : 연계시스템 시설관련 보호계전기 IED 설정","2020-04-03 09:00","2020-04-03 18:00","2020-04-03 09:00","2020-04-03 18:00","연속"]
[453,"부산울산","서부산","신김해지사#1 T/L","보호IED ~ SCADA 원격소장치 연계시스템 시설공사","선로명 : 154kV 지사-미음#1 T/L 작업내용 : 연계시스템 시설관련 보호계전기 IED 설정","2020-04-01 09:00","2020-04-02 18:00","2020-04-01 09:00","2020-04-02 18:00","매일"]
[454,"부산울산","울산","두왕영남TP#2 T/L","154㎸ 신울산-울산 등 2개T/L 지장송전선로 이설공사","1) 154㎸ 신울산-울산T/L ○ 철탑교체 : 2기(No.12, 13) ○ 전선 교체 : 11∼14호[0.945C-km, HSTACIR/AW 330㎟] 2) 154㎸ 두왕-영남TPT/L ○ 철탑교체 : 2기( No.29, 30) ○ 전선 교체 : 28∼31호[0.585C-km, HSTACIR/AW 410㎟]","2020-04-10 07:00","2020-04-11 18:00","2020-04-10 07:00","2020-04-11 18:00","연속"]
[455,"부산울산","울산","두왕영남TP#1 T/L","154㎸ 신울산-울산 등 2개T/L 지장송전선로 이설공사","1) 154㎸ 신울산-울산T/L ○ 철탑교체 : 2기(No.12, 13) ○ 전선 교체 : 11∼14호[0.945C-km, HSTACIR/AW 330㎟] 2) 154㎸ 두왕-영남TPT/L ○ 철탑교체 : 2기( No.29, 30) ○ 전선 교체 : 28∼31호[0.585C-km, HSTACIR/AW 410㎟]","2020-04-12 07:00","2020-04-17 18:00","2020-04-12 07:00","2020-04-17 18:00","연속"]
[456,"부산울산","울산","두왕영남TP#1 T/L","154㎸ 신울산-울산 등 2개T/L 지장송전선로 이설공사","1) 154㎸ 신울산-울산T/L ○ 철탑교체 : 2기(No.12, 13) ○ 전선 교체 : 11∼14호[0.945C-km, HSTACIR/AW 330㎟] 2) 154㎸ 두왕-영남TPT/L ○ 철탑교체 : 2기( No.29, 30) ○ 전선 교체 : 28∼31호[0.585C-km, HSTACIR/AW 410㎟]","2020-04-21 07:00","2020-04-21 18:00","2020-04-21 07:00","2020-04-21 18:00","연속"]
[457,"부산울산","울산","두왕영남TP#2 T/L","154㎸ 신울산-울산 등 2개T/L 지장송전선로 이설공사","1) 154㎸ 신울산-울산T/L ○ 철탑교체 : 2기(No.12, 13) ○ 전선 교체 : 11∼14호[0.945C-km, HSTACIR/AW 330㎟] 2) 154㎸ 두왕-영남TPT/L ○ 철탑교체 : 2기( No.29, 30) ○ 전선 교체 : 28∼31호[0.585C-km, HSTACIR/AW 410㎟]","2020-04-18 07:00","2020-04-20 18:00","2020-04-18 07:00","2020-04-20 18:00","연속"]
[458,"부산울산","울산","신온산성암#2 T/L","345kV 신울산복합-북부산T/L 건설공사","- 345kV 신울산복합-북부산T/L No.15~17 구간 가선공사 - 154kV 신온산-성암 #2T/L 임시선로 구성공사","2020-04-01 07:00","2020-04-13 18:00","취소","취소","연속"]
[459,"부산울산","울산","신울산명례#1 T/L","20년 상반기 개폐기 정밀점검공사","62-63 SEC CB 시험가압 1H","2020-04-24 17:00","2020-04-24 18:00","2020-04-24 17:00","2020-04-24 18:00","연속"]
[460,"부산울산","울산","신울산울산#1 T/L","154㎸ 신울산-울산 등 2개T/L 지장송전선로 이설공사","1) 154㎸ 신울산-울산T/L ○ 철탑교체 : 2기(No.12, 13) ○ 전선 교체 : 11∼14호[0.945C-km, HSTACIR/AW 330㎟] 2) 154㎸ 두왕-영남TPT/L ○ 철탑교체 : 2기( No.29, 30) ○ 전선 교체 : 28∼31호[0.585C-km, HSTACIR/AW 410㎟]","2020-04-23 07:00","2020-04-24 18:00","2020-04-23 07:00","2020-04-24 18:00","연속"]
[461,"부산울산","울산","신울산울산#2 T/L","154㎸ 신울산-울산 등 2개T/L 지장송전선로 이설공사","1) 154㎸ 신울산-울산T/L ○ 철탑교체 : 2기(No.12, 13) ○ 전선 교체 : 11∼14호[0.945C-km, HSTACIR/AW 330㎟] 2) 154㎸ 두왕-영남TPT/L ○ 철탑교체 : 2기( No.29, 30) ○ 전선 교체 : 28∼31호[0.585C-km, HSTACIR/AW 410㎟]","2020-04-21 07:00","2020-04-22 18:00","2020-04-21 07:00","2020-04-22 18:00","연속"]
[462,"부산울산","울산","신울산두왕#2 T/L","2020년도 가공송전선로 순시점검 위탁공사","□ 154kV 신울산-두왕#2T/L 정밀점검 - 대상 : 37~40(5기)","2020-04-08 08:30","2020-04-08 18:00","2020-04-08 08:30","2020-04-08 18:00","연속"]
[463,"부산울산","울산","신울산울산#2 T/L","154㎸ 신울산-울산 등 2개T/L 지장송전선로 이설공사","1) 154㎸ 신울산-울산T/L ○ 철탑교체 : 2기(No.12, 13) ○ 전선 교체 : 11∼14호[0.945C-km, HSTACIR/AW 330㎟] 2) 154㎸ 두왕-영남TPT/L ○ 철탑교체 : 2기( No.29, 30) ○ 전선 교체 : 28∼31호[0.585C-km, HSTACIR/AW 410㎟]","2020-04-08 07:00","2020-04-09 18:00","2020-04-08 07:00","2020-04-09 18:00","연속"]
[464,"부산울산","울산","신울산두왕#1 T/L","2020년도 가공송전선로 순시점검 위탁공사","(안전이격확보선로) □ 154kV 신울산-울산#1T/L 정밀점검관련 안전이격확보 - 대상설비 : 154kV 신울산-두왕#1T/L","2020-04-06 08:30","2020-04-06 18:00","2020-04-06 08:30","2020-04-06 18:00","연속"]
[465,"부산울산","울산","신울산울산#1 T/L","154㎸ 신울산-울산 등 2개T/L 지장송전선로 이설공사","1) 154㎸ 신울산-울산T/L ○ 철탑교체 : 2기(No.12, 13) ○ 전선 교체 : 11∼14호[0.945C-km, HSTACIR/AW 330㎟] 2) 154㎸ 두왕-영남TPT/L ○ 철탑교체 : 2기( No.29, 30) ○ 전선 교체 : 28∼31호[0.585C-km, HSTACIR/AW 410㎟]","2020-04-06 07:00","2020-04-07 18:00","2020-04-06 07:00","2020-04-07 18:00","연속"]
[466,"부산울산","울산","신울산S/S 154kV #63 BUS","20년 상반기 개폐기 정밀점검공사","62-63 SEC CB 시험가압 1H","2020-04-24 17:00","2020-04-24 18:00","2020-04-24 17:00","2020-04-24 18:00","연속"]
[467,"부산울산","울산","신울산S/S 154kV #62-#63 SEC CB","2020년 154kV 상반기 개폐장치 정밀점검공사","GIS 정밀점검","2020-04-23 09:00","2020-04-24 18:00","2020-04-23 09:00","2020-04-24 18:00","연속"]
[468,"부산울산","울산","신울산S/S 154kV #68 BUS","20년 상반기 개폐기 정밀점검공사","67-68 SEC CB 시험가압 1H","2020-04-28 17:00","2020-04-28 18:00","2020-04-28 17:00","2020-04-28 18:00","연속"]
[469,"부산울산","울산","신울산명례#1 T/L","20년 상반기 개폐기 정밀점검공사","67-68 SEC CB 시험가압 1H","2020-04-28 17:00","2020-04-28 18:00","2020-04-28 17:00","2020-04-28 18:00","연속"]
[470,"부산울산","울산","신울산S/S 154kV #67-#68 SEC CB","2020년 154kV 상반기 개폐장치 정밀점검공사","GIS 정밀점검","2020-04-27 09:00","2020-04-28 18:00","2020-04-27 09:00","2020-04-28 18:00","연속"]
[471,"부산울산","울산","신온산온산#3 T/L","2020년 154kV 상반기 개폐장치 정밀점검공사","- 온산S/S 154kV#4M.Tr 1차 GIS 정밀점검 후 시험가압 1H","2020-04-22 17:00","2020-04-22 18:00","2020-04-22 17:00","2020-04-22 18:00","연속"]
[472,"부산울산","울산","온산처용#2 T/L","2020년 154kV 상반기 개폐장치 정밀점검공사","온산)GIS 정밀점검 처용) 차단기 동작시험","2020-04-13 09:00","2020-04-14 18:00","2020-04-13 09:00","2020-04-14 18:00","연속"]
[473,"부산울산","울산","신온산온산#3 T/L","2020년 154kV 상반기 개폐장치 정밀점검공사","- 온산S/S 154kV#4M.Tr 1차 #2DS 정밀점검 후 시험가압 1H","2020-04-20 17:00","2020-04-20 18:00","2020-04-20 17:00","2020-04-20 18:00","연속"]
[474,"부산울산","울산","용연울산TP#3 T/L","20~21년 변전협력 총액공사","용연) 차단기 동작시험 및 전자변교체 울산T/P) 차단기 동작시험","2020-04-09 09:00","2020-04-09 18:00","2020-04-09 09:00","2020-04-09 18:00","연속"]
[475,"부산울산","울산","용연처용#1 T/L","2020년도 가공송전 순시점검 위탁공사","ㅁ 안전이격 확보를 위한 휴전 - 점검설비 : 용연-처용#2T/L","2020-04-16 10:00","2020-04-17 14:00","2020-04-24 07:00","2020-04-29 18:00","연속"]
[476,"부산울산","울산","용연울산TP#1 T/L","2020년 154kV 상반기 개폐장치 정밀점검공사","- 용연S/S 154kV#1M.Tr 1차 GIS 정밀점검 후 시험가압 1H","2020-04-03 17:00","2020-04-03 18:00","2020-04-03 17:00","2020-04-03 18:00","연속"]
[477,"부산울산","울산","용연울산TP#2 T/L","2020년 154kV 상반기 개폐장치 정밀점검공사","- 용연S/S 154kV#2M.Tr 정밀점검 후 시험가압 1H","2020-04-07 17:00","2020-04-07 18:00","2020-04-07 17:00","2020-04-07 18:00","연속"]
[478,"부산울산","울산","용연처용#2 T/L","2020년도 가공송전 순시점검 위탁공사","ㅁ 안전이격 확보를 위한 휴전 - 점검설비 : 용연-처용#1T/L","2020-04-16 08:30","2020-04-17 12:00","취소","취소","연속"]
[479,"부산울산","울산","용연처용#1 T/L","345kV 신울산복합-북부산T/L 건설공사","- 154kV 용연-처용 #1T/L 임시선로 구성공사","2020-04-16 07:00","2020-04-18 18:00","취소","취소","연속"]
[480,"부산울산","울산","용연처용#2 T/L","345kV 신울산복합-북부산T/L 건설공사","- 345kV 신울산복합-북부산T/L No.13~15 가선공사 - 154kV 용연-처용 #2T/L 본선로 구성공사","2020-04-21 07:00","2020-05-02 18:00","취소","취소","연속"]
[481,"부산울산","울산","용연울산TP#2 T/L","2020년 가공송전 순시점검 위탁공사","□ 안전이격 확보를 위한 휴전 - 대상설비 : 154kV 용연-울산TP#2T/L - 점검설비 : 154kV 용연-처용 #2T/L 정밀점검 3호","2020-04-27 08:30","2020-04-27 10:00","취소","취소","연속"]
[482,"부산울산","직할","우동대연 T/L","2020년 직할 변전협력회사 총액공사","- 우동-대연T/L GIS 보통점검","2020-04-03 10:00","2020-04-03 18:00","취소","취소","연속"]
[483,"부산울산","직할","수정범일#1 T/L","2020년 직할 변전협력회사 총액공사","- 범일S/S 범일-수정 #1T/L GIS 차단기 동작시험 - 수정S/S 범일-수정 #1T/L GIS 차단기 동작시험","2020-04-02 10:00","2020-04-02 14:00","2020-04-02 10:00","2020-04-02 14:00","연속"]
[484,"부산울산","직할","수정범일#2 T/L","2020년 직할 변전협력회사 총액공사","- 범일S/S 범일-수정 #2T/L GIS 차단기 동작시험 - 수정S/S 범일-수정 #2T/L GIS 차단기 동작시험","2020-04-02 14:00","2020-04-02 18:00","2020-04-02 14:00","2020-04-02 18:00","연속"]
[485,"부산울산","직할","범일서면#2 T/L","2020년 직할 변전협력회사 총액공사","- 범일S/S 범일-서면 #2T/L GIS 차단기 동작시험 - 서면S/S 범일-서면 #2T/L GIS 차단기 동작시험","2020-04-01 14:00","2020-04-01 18:00","2020-04-01 14:00","2020-04-01 18:00","연속"]
[486,"부산울산","직할","범일서면#1 T/L","2020년 직할 변전협력회사 총액공사","- 범일S/S 범일-서면 #1T/L GIS 차단기 동작시험 - 서면S/S 범일-서면 #1T/L GIS 차단기 동작시험","2020-04-01 10:00","2020-04-01 14:00","2020-04-01 10:00","2020-04-01 14:00","연속"]
[487,"부산울산","직할","부산수정#1 T/L","2020년 직할 변전협력회사 총액공사","- 부산S/S 부산-수정 #1T/L GIS 차단기 동작시험 - 수정S/S 부산-수정 #1T/L GIS 차단기 동작시험","2020-04-06 10:00","2020-04-06 14:00","2020-04-06 10:00","2020-04-06 14:00","연속"]
[488,"부산울산","직할","부산수정#2 T/L","2020년 직할 변전협력회사 총액공사","- 부산S/S 부산-수정 #2T/L GIS 차단기 동작시험 - 수정S/S 부산-수정 #2T/L GIS 차단기 동작시험","2020-04-06 14:00","2020-04-06 18:00","2020-04-06 14:00","2020-04-06 18:00","연속"]
[489,"부산울산","동부산","수영정보#2 T/L","수영S/S 154kV GIS 차단기 동작시험","1.수영S/S 154kV GIS 차단기 동작시험(수영-정보#2T/L) 2.정보S/S 154kV GIS 차단기 동작시험","2020-04-13 09:30","2020-04-13 14:00","취소","취소","연속"]
[490,"경남","직할","녹공마천#2 T/L","마천S/S 154kV 녹공-마천#2T/L GIS 조작시험","마천S/S 154kV 녹공-마천#2T/L GIS 조작시험","2020-04-09 13:30","2020-04-09 17:30","2020-04-09 13:30","2020-04-09 17:30","연속"]
[491,"경남","직할","녹공마천#1 T/L","마천S/S 154kV 녹공-마천#1T/L GIS 조작시험","마천S/S 154kV 녹공-마천#1T/L GIS 조작시험","2020-04-09 09:30","2020-04-09 13:30","2020-04-09 09:30","2020-04-09 13:30","연속"]
[492,"경남","직할","마천진해#2 T/L","마천, 진해S/S 154kV 마천-진해#2T/L 개폐장치 조작시험","마천, 진해S/S 154kV 마천-진해#2T/L 개폐장치 조작시험","2020-04-01 08:30","2020-04-01 17:30","2020-04-01 08:30","2020-04-01 17:30","연속"]
[493,"경남","직할","삼정천선#1 T/L","삼정S/S 154kV 삼정-천선#1T/L 인출변경","삼정S/S 옥외철구 현대화 사업 - 삼정S/S측 154kV 삼정-천선#1T/L 인출변경(옥외철구-&gtGIS)","2020-04-20 09:30","2020-05-10 18:30","취소","취소","연속"]
[494,"경남","직할","신월삼정#2 T/L","154kV 신월-삼정#2T/L OF케이블 절연유 채유","154kV 신월-삼정#2T/L OF케이블 절연유 분석을 위한 채유","2020-04-29 14:00","2020-04-29 18:00","2020-04-29 14:00","2020-04-29 18:00","연속"]
[495,"경남","직할","신월삼정#1 T/L","154kV 신월-삼정#1T/L OF케이블 절연유 채유","154kV 신월-삼정#1T/L OF케이블 절연유 분석을 위한 채유","2020-04-29 09:00","2020-04-29 14:00","2020-04-29 09:00","2020-04-29 14:00","연속"]
[496,"경남","직할","신김해주촌#2 T/L","주촌S/S 154kV 신김해-주촌#2T/L GIS 보통점검","주촌S/S 154kV 신김해-주촌#2T/L GIS 보통점검 신김해S/S 154kV 신김해-주촌#2T/L GIS 조작시험","2020-04-28 09:30","2020-04-28 17:30","2020-04-28 09:30","2020-04-28 17:30","연속"]
[497,"경남","직할","신김해주촌#1 T/L","주촌S/S 154kV 신김해-주촌#1T/L GIS 보통점검","주촌S/S 154kV 신김해-주촌#1T/L GIS 보통점검 신김해S/S 154kV 신김해-주촌#1T/L GIS 조작시험","2020-04-27 09:30","2020-04-27 17:30","2020-04-27 09:30","2020-04-27 17:30","연속"]
[498,"경남","직할","마천진해#1 T/L","2020년도 가공송전 순시점검 위탁공사","송전선로 초기점검(1,2호)","2020-04-01 08:00","2020-04-01 13:00","2020-04-01 08:00","2020-04-01 13:00","매일"]
[499,"경남","직할","차룡창공#1 T/L","차룡S/S 154kV 차룡-창공#1T/L GIS 조작시험","차룡S/S 154kV 차룡-창공#1T/L GIS 조작시험 및 전자변 교체","2020-04-06 09:30","2020-04-06 17:30","취소","취소","연속"]
[500,"경남","진주","사천개양#1 T/L","154kV 사천-개양T/L No.8 안전이격거리 확보(인클로징)공사","○ 154kV 사천-개양#1,2T/L No.8 안전이격거리 확보공사 - 인클로징 철탑조립 및 전력선 교체(No.7~10, 0.849 c-km) ※ 진주 송전정비회사 사천-개양T/L 2회선 수평배열구간 애자련 교체작업 병행시행 예정","2020-04-30 07:00","2020-05-01 18:00","2020-04-30 07:00","2020-05-01 18:00","연속"]
[501,"경남","진주","사천개양#2 T/L","154kV 사천-개양T/L No.8 안전이격거리 확보(인클로징)공사","○ 154kV 사천-개양#1,2T/L No.8 안전이격거리 확보공사 - 인클로징 철탑조립 및 전력선 교체(No.7~10, 0.849 c-km) ※ 진주 송전정비회사 사천-개양T/L 2회선 수평배열구간 애자련 교체작업 병행시행 예정","2020-04-30 07:00","2020-05-02 18:00","2020-04-30 07:00","2020-05-02 18:00","연속"]
[502,"경남","진주","거창S/S 154kV #60-#65 BUS TIE CB","거창S/S 154kV #1 BUS TIE(6100) 보통점검","거창S/S 154kV #1 BUS TIE(6100) 보통점검","2020-04-02 10:00","2020-04-02 14:00","2020-04-02 10:00","2020-04-02 14:00","연속"]
[503,"경남","진주","가야사봉#2 T/L","사봉S/S 154kV 가야-사봉#2T/L CB(627) 보통점검","사봉S/S 154kV 가야-사봉#2T/L CB(627) 보통점검","2020-04-11 10:00","2020-04-11 14:00","2020-04-11 10:00","2020-04-11 14:00","연속"]
[504,"경남","진주","광양하동#1 T/L","하동S/S 154kV 광양-하동#1T/L CB(677) 보통점검","하동S/S 154kV 광양-하동#1T/L CB(677) 보통점검 하동S/S 154kV 광양-하동#1T/L PT, LA(A,B,C) 보통점검","2020-04-23 10:00","2020-04-23 14:00","2020-04-13 10:00","2020-04-13 14:00","연속"]
[505,"경남","진주","광양하동#2 T/L","하동S/S 154kV 광양-하동#2T/L CB(687) 보통점검","하동S/S 154kV 광양-하동#2T/L CB(687) 보통점검 하동S/S 154kV 광양-하동#2T/L PT, LA(A,B,C) 보통점검","2020-04-23 14:00","2020-04-23 17:00","2020-04-13 14:00","2020-04-13 17:00","연속"]
[506,"경남","진주","합천S/S 154kV #60-#65 BUS TIE CB","합천S/S 154kV #1 BUS TIE(6100) 보통점검","합천S/S 154kV #1 BUS TIE(6100) 보통점검","2020-04-24 10:00","2020-04-24 14:00","2020-04-24 10:00","2020-04-24 14:00","연속"]
[507,"경남","통영","통영거제#2 T/L","거제S/S #4M.Tr 1차 GIS 정밀점검 시험가압","거제S/S #4M.Tr 1차 GIS 정밀점검 시험가압","2020-04-10 07:00","2020-04-10 08:00","2020-04-10 07:00","2020-04-10 08:00","연속"]
[508,"경남","통영","통영거제#2 T/L","거제S/S #3M.Tr 1차 GIS 정밀점검 시험가압","거제S/S #3M.Tr 1차 GIS 정밀점검 시험가압","2020-04-08 07:00","2020-04-08 08:00","2020-04-08 07:00","2020-04-08 08:00","연속"]
[509,"경남","통영","신고성통영 T/L","154kV 신고성-통영T/L 보수작업","154kV 신고성-통영T/L 불량개소 보수작업(97호)","2020-04-12 09:00","2020-04-12 18:00","2020-04-12 09:00","2020-04-12 18:00","연속"]
[510,"경남","통영","통영거제#2 T/L","통영S/S #4M.Tr 1차 GIS 정밀점검 시험가압","통영S/S #4M.Tr 1차 GIS 정밀점검 시험가압","2020-04-18 09:00","2020-04-18 10:00","2020-04-18 09:00","2020-04-18 10:00","연속"]
[511,"경남","통영","통영거제#1 T/L","154kV 통영-거제T/L 보수작업","154kV 통영-거제T/L 불량개소 보수작업(3호)","2020-04-12 09:00","2020-04-12 18:00","2020-04-12 09:00","2020-04-12 18:00","연속"]
[512,"경남","통영","통영거제#2 T/L","통영S/S 154kV #60-65 BUS TIE GIS 정밀점검 시험가압","통영S/S 154kV #60-65 BUS TIE GIS 정밀점검 시험가압","2020-04-22 07:00","2020-04-22 08:00","2020-04-22 07:00","2020-04-22 08:00","연속"]
[513,"경남","함안","신마산동읍#2 T/L","154kV 신마산-동읍#2T/L, 신마산-차룡#1T/L 정밀점검","154kV 신마산-동읍#2T/L, 신마산-차룡#1T/L 정밀점검 (병가구간 1호~38호)","2020-04-07 08:00","2020-04-16 18:00","취소","취소","매일"]
[514,"경남","함안","동읍S/S 154kV 신월-동읍#2T/L GIS","동읍S/S 154kV 신월-동읍#2T/L GIS 정밀점검","동읍S/S 154kV 신월-동읍#2T/L GIS 정밀점검","2020-04-22 08:30","2020-04-23 17:30","2020-04-22 08:30","2020-04-23 17:30","연속"]
[515,"경남","함안","동읍S/S 154kV 신월-동읍#1T/L GIS","동읍S/S 154kV 신월-동읍#1T/L GIS 정밀점검","동읍S/S 154kV 신월-동읍#1T/L GIS 정밀점검","2020-04-20 08:30","2020-04-21 17:30","2020-04-20 08:30","2020-04-21 17:30","연속"]
[516,"경남","함안","밀양S/S 154kV 초동-밀양#2T/L GIS","밀양S/S 154kV #4M.Tr 1차 GIS 정밀점검","밀양S/S 154kV #4M.Tr 1차 GIS 정밀점검 관련 시험가압","2020-04-14 16:00","2020-04-14 17:30","취소","취소","연속"]
[517,"경남","함안","수산S/S 154kV 진영-수산#1T/L GIS","수산S/S 154kV 진영-수산#1T/L GIS 조작시험","수산S/S 154kV 진영-수산#1T/L GIS 조작시험","2020-04-27 09:30","2020-04-27 13:30","취소","취소","연속"]
[518,"경남","함안","수산S/S 154kV 진영-수산#2T/L GIS","수산S/S 154kV 진영-수산#2T/L GIS 조작시험","수산S/S 154kV 진영-수산#2T/L GIS 조작시험","2020-04-27 13:30","2020-04-27 17:30","2020-04-28 08:30","2020-04-29 17:30","연속"]
[519,"경남","함안","수출S/S 154kV 수출-월림#1T/L GIS","수출S/S 154kV 수출-월림#1T/L GIS 정밀점검","수출S/S 154kV 수출-월림#1T/L GIS 정밀점검","2020-04-09 08:30","2020-04-10 17:30","취소","취소","연속"]
[520,"경남","함안","수출S/S 154kV 수출-월림#2T/L GIS","수출S/S 154kV 수출-월림#2T/L GIS 정밀점검","수출S/S 154kV 수출-월림#2T/L GIS 정밀점검","2020-04-07 08:30","2020-04-08 17:30","취소","취소","연속"]
[521,"경남","함안","신마산마산#2 T/L","154kV 신마산-서마산T/L 전선교체공사 안전이격 휴전","10~13호 전선교체 안전이격 휴전","2020-04-01 06:30","2020-04-03 18:00","취소","취소","연속"]
[522,"경남","함안","신마산마산#1 T/L","154kV 신마산-서마산T/L 전선교체공사 안전이격 휴전","10~13호 전선교체 안전이격 휴전","2020-04-04 06:30","2020-04-06 18:00","취소","취소","연속"]
[523,"경남","함안","신마산차룡#1 T/L","154kV 의창변전소 건설사업","신마산-차룡#1T/L 분기접속 공사 및 변전소 최초가압","2020-04-07 09:00","2020-05-03 18:00","취소","취소","연속"]
[524,"경남","함안","중리S/S 154kV 중리-가야#1T/L GIS","중리S/S 154kV #1M.Tr 1차 GIS 정밀점검","중리S/S 154kV #1M.Tr 1차 GIS 정밀점검 관련 시험가압","2020-04-25 16:00","2020-04-25 17:30","2020-04-25 16:00","2020-04-25 17:30","연속"]
[525,"경남","함안","중리S/S 154kV 중리-가야#2T/L GIS","중리S/S 154kV #2M.Tr 1차 GIS 정밀점검","중리S/S 154kV #2M.Tr 1차 GIS 정밀점검 관련 시험가압","2020-04-18 16:00","2020-04-18 17:30","2020-04-18 16:00","2020-04-18 17:30","연속"]
[526,"경남","함안","창녕S/S 154kV 창녕-초동#1T/L CB","창녕S/S 154kV 창녕-초동#1T/L GCB 보통점검","창녕S/S 154kV 창녕-초동#1T/L GCB 보통점검","2020-04-23 09:30","2020-04-23 17:30","2020-04-23 09:30","2020-04-23 17:30","연속"]
[527,"경남","함안","창녕S/S 154kV 창녕-초동#2T/L CB","창녕S/S 154kV 창녕-초동#2T/L GCB 보통점검","창녕S/S 154kV 창녕-초동#2T/L GCB 보통점검","2020-04-24 09:30","2020-04-24 17:30","2020-04-24 09:30","2020-04-24 17:30","연속"]
[528,"경남","함안","칠서S/S 154kV 신마산-칠서#1T/L GIS","칠서SS 154kV 신마산-칠서#1T/L, #2M.Tr 1차 GIS 대체","칠서S/S 154kV 신마산-칠서#1T/L, #2M.Tr 1차 GIS 대체","2020-04-06 09:00","2020-04-26 18:00","2020-04-06 09:00","2020-04-26 18:00","연속"]
[529,"경남","함안","칠서S/S 154kV #60 BUS","칠서SS 154kV 신마산-칠서#1T/L, #2M.Tr 1차 GIS 대체","칠서S/S 154kV 신마산-칠서#1T/L, #2M.Tr 1차 GIS 대체","2020-04-08 09:00","2020-04-18 13:30","2020-04-08 09:00","2020-04-18 13:30","연속"]
[530,"남서울","동서울","위례위례열병합#2T/L CB","위례열병합발전소 정비기간중 설비점검","위례열병합발전소 정비기간중 설비점검","2020-04-08 09:00","2020-04-09 18:00","2020-04-08 09:00","2020-04-09 18:00","연속"]
[531,"남서울","직할","노들노량진 T/L","170kV GIS 보통점검","170kV GIS 보통점검","2020-04-17 10:00","2020-04-17 18:00","2020-04-17 10:00","2020-04-17 18:00","연속"]
[532,"충북",null,"충주충주HP#2 T/L","주 전력량계(0.2급) 오차시험","주 전력량계(0.2급) 오차시험","2020-04-02 09:00","2020-04-02 18:00","2020-04-02 09:00","2020-04-02 18:00","연속"]
[533,"광주전남",null,"승주주암HP T/L","옥외변전설비 정기점검","옥외변전설비 정기점검","2020-04-22 09:00","2020-04-22 18:00","2020-04-22 09:00","2020-04-22 18:00","연속"]
[534,"광주전남",null,"서순천주암HP#1 T/L","옥외변전설비 정기점검","옥외변전설비 정기점검","2020-04-22 09:00","2020-04-22 18:00","2020-04-22 09:00","2020-04-22 18:00","연속"]

{"sheet":"시송전설비","index":4,"n_rows":1,"n_cols":17,"rows_kept":1,"cut":false,"hidden":true,"merged":[[0,16,0,21]]}
["1차\n사업소","2차\n사업소","설비명",{"$nulls":8},"연간\n반영","비고","Key-point","시송전설비 여부","찾는함수","=IF(ISERROR(VLOOKUP(D5,시송전설비!$C$2:$O$130,13,0)),\"-\",VLOOKUP(D5,시송전설비!$C$2:$O$130,13,0))"]